## Standards and Conversion
NASA Standard Atmosphere
https://ntrs.nasa.gov/citations/19770009539
Table 1 Data for Standard Atmosphere byi Altitude
| Table 1: P(mb) vs. altitude in meters | Pressure |  |  |  | Density
| m | mb = 100 n/m2 | Inches HG | PSI | kPA | (kg/m3) | lb/ft3
| 0 | 1013.25 | 29.9213 | 14.6959 | 101.325 | 1.225 | 0.076474
| 50 | 1007.2 | 29.7426 | 14.6082 | 100.72 | 1.2191 | 0.076106
| 100 | 1001.2 | 29.5654 | 14.5212 | 100.12 | 1.2133 | 0.075744
| 150 | 995.35 | 29.3927 | 14.4363 | 99.535 | 1.2075 | 0.075382
| 200 | 989.45 | 29.2184 | 14.3508 | 98.945 | 1.2017 | 0.07502
| 250 | 983.57 | 29.0448 | 14.2655 | 98.357 | 1.1959 | 0.074658
| 300 | 977.72 | 28.8721 | 14.1806 | 97.772 | 1.1901 | 0.074296
| 350 | 971.9 | 28.7002 | 14.0962 | 97.19 | 1.1844 | 0.07394
| 400 | 966.11 | 28.5292 | 14.0122 | 96.611 | 1.1786 | 0.073578
| 450 | 960.34 | 28.3588 | 13.9286 | 96.034 | 1.173 | 0.073228
| 500 | 954.61 | 28.1896 | 13.8454 | 95.461 | 1.1673 | 0.072872
STANDARD ATMOSPHERE,page xiv
See also National institute of standards conversion factor table
https://www.nist.gov/pml/special-publication-811/nist-guide-si-appendix-b-conversion-factors/nist-guide-si-appendix-b8
Converting N/m2 to PSI
Pound force = force sufficient to accelerate mass of one pound at 32 ft/sec2
Newton force = force sufficient to accelerate one kg at 1 m/sec2
| Gravitational acceleration (32 feet) = |  | 9.8066 | m/sec2
| Pound = |  | 0.45359 | kg
| So, pound force per newton |  | 4.4482
| Inches2 per meter 2 |  | 1550.0031
Pascal = 1 n/m2
| Pascal per PSI |  | 6894.7577

## phi vs W
Humidity ratio (mass water/mass dry air), W, from pressure, temperature and Rh, using W_ptphi_HAP_IP
Temperature F
Relative Humidity (phi) | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
10 | 0.00034383 | 0.00051772 | 0.00075786 | 0.0010914 | 0.001548 | 0.0021643 | 0.0029858 | 0.0040678
20 | 0.00068804 | 0.0010363 | 0.0015176 | 0.0021867 | 0.0031037 | 0.0043438 | 0.0060004 | 0.0081892
30 | 0.0010326 | 0.0015557 | 0.0022791 | 0.0032858 | 0.0046672 | 0.0065385 | 0.0090442 | 0.012365
40 | 0.0013776 | 0.0020761 | 0.0030426 | 0.0043888 | 0.0062385 | 0.0087486 | 0.012118 | 0.016597
50 | 0.001723 | 0.0025972 | 0.0038079 | 0.0054957 | 0.0078177 | 0.010974 | 0.015221 | 0.020885
60 | 0.0020687 | 0.0031193 | 0.004575 | 0.0066066 | 0.0094049 | 0.013216 | 0.018355 | 0.025232
70 | 0.0024148 | 0.0036422 | 0.0053441 | 0.0077213 | 0.011 | 0.015473 | 0.021521 | 0.029638
80 | 0.0027613 | 0.004166 | 0.0061151 | 0.00884 | 0.012603 | 0.017747 | 0.024717 | 0.034104
90 | 0.0031082 | 0.0046907 | 0.0068879 | 0.0099628 | 0.014215 | 0.020037 | 0.027946 | 0.038632
100 | 0.0034555 | 0.0052163 | 0.0076627 | 0.011089 | 0.015835 | 0.022343 | 0.031206 | 0.043222 | Saturation W
Validation 1
Reproduce Engineering Tool Box -- Moist Air, Weight of Water Vapor
https://www.engineeringtoolbox.com/water-vapor-air-d_854.html
Grains water vapor per pound mixture
Temperature F
Relative Humidity | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
10 | 2.4068 | 3.624 | 5.305 | 7.64 | 10.8359 | 15.1502 | 20.9006 | 28.4747
20 | 4.8163 | 7.2541 | 10.623 | 15.3069 | 21.7258 | 30.4063 | 42.0029 | 57.3243
30 | 7.2284 | 10.8902 | 15.954 | 23.0008 | 32.6703 | 45.7693 | 63.3097 | 86.5563
40 | 9.6432 | 14.5324 | 21.298 | 30.7218 | 43.6696 | 61.2403 | 84.8242 | 116.1784
50 | 12.0607 | 18.1807 | 26.6551 | 38.4702 | 54.7242 | 76.8206 | 106.5492 | 146.1983
60 | 14.4808 | 21.8351 | 32.0253 | 46.2459 | 65.8346 | 92.5111 | 128.488 | 176.6242
70 | 16.9037 | 25.4956 | 37.4087 | 54.0493 | 77.0011 | 108.3133 | 150.6436 | 207.4644
80 | 19.3292 | 29.1622 | 42.8054 | 61.8803 | 88.2241 | 124.2281 | 173.0194 | 238.7273
90 | 21.7575 | 32.835 | 48.2153 | 69.7393 | 99.5042 | 140.2569 | 195.6186 | 270.4218
100 | 24.1884 | 36.5139 | 53.6386 | 77.6262 | 110.8417 | 156.4008 | 218.4445 | 302.5568
Validation 2
Round trip computation of Relative humidity from pTW using phi_ptW_HAP_IP (Exact!)
Temperature F
Expected Relative Humidity | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Validation 3
Compare Saturated line to Table 2 in 2021 Ashrae handbook
| 0.0034555 | 0.0052163 | 0.0076627 | 0.011089 | 0.015835 | 0.022343 | 0.031206 | 0.043222
Diff | 1.7499e-08 | 2.8301e-08 | 4.6577e-08 | -4.6355e-07 | 4.7116e-07 | 2.196e-08 | -3.6386e-07 | -3.9731e-07

## specific heat
Specific Heat Capacity of Moist Air (Isobaric) from cp_ptW_HAP_IP
Assumed Pressure | [10 empty] | 14.6959 | PSI (Standard atmosphere)
Relative Humidity
Temperature F | 0% | 2% | 4% | 6% | 8% | 10% | 12% | 14% | 16% | 18% | 20% | 22% | 24% | 26% | 28% | 30% | 32% | 34% | 36% | 38% | 40% | 42% | 44% | 46% | 48% | 50% | 52% | 54% | 56% | 58% | 60% | 62% | 64% | 66% | 68% | 70% | 100%
55 | 0.24026 | 0.2403 | 0.24034 | 0.24037 | 0.24041 | 0.24045 | 0.24049 | 0.24052 | 0.24056 | 0.2406 | 0.24064 | 0.24068 | 0.24071 | 0.24075 | 0.24079 | 0.24083 | 0.24087 | 0.2409 | 0.24094 | 0.24098 | 0.24102 | 0.24106 | 0.2411 | 0.24113 | 0.24117 | 0.24121 | 0.24125 | 0.24129 | 0.24133 | 0.24137 | 0.2414 | 0.24144 | 0.24148 | 0.24152 | 0.24156 | 0.2416 | 0.24219
56 | 0.24026 | 0.2403 | 0.24034 | 0.24038 | 0.24042 | 0.24046 | 0.2405 | 0.24054 | 0.24058 | 0.24062 | 0.24066 | 0.24069 | 0.24073 | 0.24077 | 0.24081 | 0.24085 | 0.24089 | 0.24093 | 0.24097 | 0.24101 | 0.24105 | 0.24109 | 0.24113 | 0.24117 | 0.24121 | 0.24125 | 0.24129 | 0.24133 | 0.24137 | 0.24141 | 0.24145 | 0.24149 | 0.24153 | 0.24157 | 0.24161 | 0.24165 | 0.24227
57 | 0.24027 | 0.24031 | 0.24035 | 0.24039 | 0.24043 | 0.24047 | 0.24051 | 0.24055 | 0.24059 | 0.24063 | 0.24067 | 0.24071 | 0.24075 | 0.2408 | 0.24084 | 0.24088 | 0.24092 | 0.24096 | 0.241 | 0.24104 | 0.24108 | 0.24112 | 0.24117 | 0.24121 | 0.24125 | 0.24129 | 0.24133 | 0.24137 | 0.24142 | 0.24146 | 0.2415 | 0.24154 | 0.24158 | 0.24162 | 0.24167 | 0.24171 | 0.24234
58 | 0.24027 | 0.24031 | 0.24035 | 0.2404 | 0.24044 | 0.24048 | 0.24052 | 0.24056 | 0.24061 | 0.24065 | 0.24069 | 0.24073 | 0.24078 | 0.24082 | 0.24086 | 0.2409 | 0.24095 | 0.24099 | 0.24103 | 0.24107 | 0.24112 | 0.24116 | 0.2412 | 0.24125 | 0.24129 | 0.24133 | 0.24138 | 0.24142 | 0.24146 | 0.2415 | 0.24155 | 0.24159 | 0.24163 | 0.24168 | 0.24172 | 0.24177 | 0.24243
59 | 0.24027 | 0.24032 | 0.24036 | 0.2404 | 0.24045 | 0.24049 | 0.24054 | 0.24058 | 0.24062 | 0.24067 | 0.24071 | 0.24075 | 0.2408 | 0.24084 | 0.24089 | 0.24093 | 0.24097 | 0.24102 | 0.24106 | 0.24111 | 0.24115 | 0.2412 | 0.24124 | 0.24129 | 0.24133 | 0.24137 | 0.24142 | 0.24146 | 0.24151 | 0.24155 | 0.2416 | 0.24164 | 0.24169 | 0.24173 | 0.24178 | 0.24182 | 0.24251
60 | 0.24028 | 0.24032 | 0.24037 | 0.24041 | 0.24046 | 0.2405 | 0.24055 | 0.24059 | 0.24064 | 0.24068 | 0.24073 | 0.24078 | 0.24082 | 0.24087 | 0.24091 | 0.24096 | 0.241 | 0.24105 | 0.2411 | 0.24114 | 0.24119 | 0.24123 | 0.24128 | 0.24133 | 0.24137 | 0.24142 | 0.24147 | 0.24151 | 0.24156 | 0.2416 | 0.24165 | 0.2417 | 0.24174 | 0.24179 | 0.24184 | 0.24189 | 0.2426
61 | 0.24028 | 0.24033 | 0.24038 | 0.24042 | 0.24047 | 0.24052 | 0.24056 | 0.24061 | 0.24066 | 0.2407 | 0.24075 | 0.2408 | 0.24084 | 0.24089 | 0.24094 | 0.24099 | 0.24103 | 0.24108 | 0.24113 | 0.24118 | 0.24122 | 0.24127 | 0.24132 | 0.24137 | 0.24142 | 0.24146 | 0.24151 | 0.24156 | 0.24161 | 0.24166 | 0.24171 | 0.24175 | 0.2418 | 0.24185 | 0.2419 | 0.24195 | 0.24269
62 | 0.24029 | 0.24033 | 0.24038 | 0.24043 | 0.24048 | 0.24053 | 0.24058 | 0.24062 | 0.24067 | 0.24072 | 0.24077 | 0.24082 | 0.24087 | 0.24092 | 0.24097 | 0.24102 | 0.24107 | 0.24111 | 0.24116 | 0.24121 | 0.24126 | 0.24131 | 0.24136 | 0.24141 | 0.24146 | 0.24151 | 0.24156 | 0.24161 | 0.24166 | 0.24171 | 0.24176 | 0.24181 | 0.24186 | 0.24191 | 0.24196 | 0.24201 | 0.24278
63 | 0.24029 | 0.24034 | 0.24039 | 0.24044 | 0.24049 | 0.24054 | 0.24059 | 0.24064 | 0.24069 | 0.24074 | 0.24079 | 0.24084 | 0.24089 | 0.24094 | 0.241 | 0.24105 | 0.2411 | 0.24115 | 0.2412 | 0.24125 | 0.2413 | 0.24135 | 0.2414 | 0.24146 | 0.24151 | 0.24156 | 0.24161 | 0.24166 | 0.24171 | 0.24177 | 0.24182 | 0.24187 | 0.24192 | 0.24198 | 0.24203 | 0.24208 | 0.24287
64 | 0.24029 | 0.24035 | 0.2404 | 0.24045 | 0.2405 | 0.24055 | 0.2406 | 0.24066 | 0.24071 | 0.24076 | 0.24081 | 0.24087 | 0.24092 | 0.24097 | 0.24102 | 0.24108 | 0.24113 | 0.24118 | 0.24124 | 0.24129 | 0.24134 | 0.2414 | 0.24145 | 0.2415 | 0.24156 | 0.24161 | 0.24166 | 0.24172 | 0.24177 | 0.24182 | 0.24188 | 0.24193 | 0.24199 | 0.24204 | 0.24209 | 0.24215 | 0.24297
65 | 0.2403 | 0.24035 | 0.2404 | 0.24046 | 0.24051 | 0.24057 | 0.24062 | 0.24067 | 0.24073 | 0.24078 | 0.24084 | 0.24089 | 0.24095 | 0.241 | 0.24105 | 0.24111 | 0.24116 | 0.24122 | 0.24127 | 0.24133 | 0.24138 | 0.24144 | 0.24149 | 0.24155 | 0.24161 | 0.24166 | 0.24172 | 0.24177 | 0.24183 | 0.24188 | 0.24194 | 0.242 | 0.24205 | 0.24211 | 0.24216 | 0.24222 | 0.24307
66 | 0.2403 | 0.24036 | 0.24041 | 0.24047 | 0.24052 | 0.24058 | 0.24064 | 0.24069 | 0.24075 | 0.2408 | 0.24086 | 0.24092 | 0.24097 | 0.24103 | 0.24109 | 0.24114 | 0.2412 | 0.24126 | 0.24131 | 0.24137 | 0.24143 | 0.24148 | 0.24154 | 0.2416 | 0.24166 | 0.24171 | 0.24177 | 0.24183 | 0.24189 | 0.24194 | 0.242 | 0.24206 | 0.24212 | 0.24218 | 0.24223 | 0.24229 | 0.24318
67 | 0.24031 | 0.24036 | 0.24042 | 0.24048 | 0.24054 | 0.24059 | 0.24065 | 0.24071 | 0.24077 | 0.24083 | 0.24088 | 0.24094 | 0.241 | 0.24106 | 0.24112 | 0.24118 | 0.24124 | 0.24129 | 0.24135 | 0.24141 | 0.24147 | 0.24153 | 0.24159 | 0.24165 | 0.24171 | 0.24177 | 0.24183 | 0.24189 | 0.24195 | 0.24201 | 0.24207 | 0.24213 | 0.24219 | 0.24225 | 0.24231 | 0.24237 | 0.24329
68 | 0.24031 | 0.24037 | 0.24043 | 0.24049 | 0.24055 | 0.24061 | 0.24067 | 0.24073 | 0.24079 | 0.24085 | 0.24091 | 0.24097 | 0.24103 | 0.24109 | 0.24115 | 0.24121 | 0.24127 | 0.24133 | 0.24139 | 0.24146 | 0.24152 | 0.24158 | 0.24164 | 0.2417 | 0.24176 | 0.24182 | 0.24189 | 0.24195 | 0.24201 | 0.24207 | 0.24213 | 0.2422 | 0.24226 | 0.24232 | 0.24238 | 0.24245 | 0.2434
69 | 0.24031 | 0.24037 | 0.24044 | 0.2405 | 0.24056 | 0.24062 | 0.24068 | 0.24075 | 0.24081 | 0.24087 | 0.24093 | 0.241 | 0.24106 | 0.24112 | 0.24118 | 0.24125 | 0.24131 | 0.24137 | 0.24144 | 0.2415 | 0.24156 | 0.24163 | 0.24169 | 0.24175 | 0.24182 | 0.24188 | 0.24195 | 0.24201 | 0.24207 | 0.24214 | 0.2422 | 0.24227 | 0.24233 | 0.2424 | 0.24246 | 0.24253 | 0.24351
70 | 0.24032 | 0.24038 | 0.24045 | 0.24051 | 0.24057 | 0.24064 | 0.2407 | 0.24077 | 0.24083 | 0.24089 | 0.24096 | 0.24102 | 0.24109 | 0.24115 | 0.24122 | 0.24128 | 0.24135 | 0.24141 | 0.24148 | 0.24155 | 0.24161 | 0.24168 | 0.24174 | 0.24181 | 0.24188 | 0.24194 | 0.24201 | 0.24207 | 0.24214 | 0.24221 | 0.24227 | 0.24234 | 0.24241 | 0.24248 | 0.24254 | 0.24261 | 0.24363
71 | 0.24032 | 0.24039 | 0.24045 | 0.24052 | 0.24059 | 0.24065 | 0.24072 | 0.24079 | 0.24085 | 0.24092 | 0.24099 | 0.24105 | 0.24112 | 0.24119 | 0.24125 | 0.24132 | 0.24139 | 0.24146 | 0.24153 | 0.24159 | 0.24166 | 0.24173 | 0.2418 | 0.24187 | 0.24193 | 0.242 | 0.24207 | 0.24214 | 0.24221 | 0.24228 | 0.24235 | 0.24242 | 0.24249 | 0.24256 | 0.24263 | 0.24269 | 0.24375
72 | 0.24033 | 0.24039 | 0.24046 | 0.24053 | 0.2406 | 0.24067 | 0.24074 | 0.24081 | 0.24088 | 0.24094 | 0.24101 | 0.24108 | 0.24115 | 0.24122 | 0.24129 | 0.24136 | 0.24143 | 0.2415 | 0.24157 | 0.24164 | 0.24171 | 0.24178 | 0.24185 | 0.24192 | 0.242 | 0.24207 | 0.24214 | 0.24221 | 0.24228 | 0.24235 | 0.24242 | 0.24249 | 0.24257 | 0.24264 | 0.24271 | 0.24278 | 0.24388
73 | 0.24033 | 0.2404 | 0.24047 | 0.24054 | 0.24061 | 0.24068 | 0.24076 | 0.24083 | 0.2409 | 0.24097 | 0.24104 | 0.24111 | 0.24119 | 0.24126 | 0.24133 | 0.2414 | 0.24147 | 0.24155 | 0.24162 | 0.24169 | 0.24177 | 0.24184 | 0.24191 | 0.24198 | 0.24206 | 0.24213 | 0.24221 | 0.24228 | 0.24235 | 0.24243 | 0.2425 | 0.24258 | 0.24265 | 0.24272 | 0.2428 | 0.24287 | 0.24401
74 | 0.24033 | 0.24041 | 0.24048 | 0.24055 | 0.24063 | 0.2407 | 0.24077 | 0.24085 | 0.24092 | 0.241 | 0.24107 | 0.24114 | 0.24122 | 0.24129 | 0.24137 | 0.24144 | 0.24152 | 0.24159 | 0.24167 | 0.24174 | 0.24182 | 0.24189 | 0.24197 | 0.24205 | 0.24212 | 0.2422 | 0.24227 | 0.24235 | 0.24243 | 0.2425 | 0.24258 | 0.24266 | 0.24273 | 0.24281 | 0.24289 | 0.24297 | 0.24414
75 | 0.24034 | 0.24041 | 0.24049 | 0.24057 | 0.24064 | 0.24072 | 0.24079 | 0.24087 | 0.24095 | 0.24102 | 0.2411 | 0.24118 | 0.24125 | 0.24133 | 0.24141 | 0.24149 | 0.24156 | 0.24164 | 0.24172 | 0.2418 | 0.24188 | 0.24195 | 0.24203 | 0.24211 | 0.24219 | 0.24227 | 0.24235 | 0.24243 | 0.2425 | 0.24258 | 0.24266 | 0.24274 | 0.24282 | 0.2429 | 0.24298 | 0.24306 | 0.24428
76 | 0.24034 | 0.24042 | 0.2405 | 0.24058 | 0.24066 | 0.24074 | 0.24081 | 0.24089 | 0.24097 | 0.24105 | 0.24113 | 0.24121 | 0.24129 | 0.24137 | 0.24145 | 0.24153 | 0.24161 | 0.24169 | 0.24177 | 0.24185 | 0.24193 | 0.24201 | 0.24209 | 0.24218 | 0.24226 | 0.24234 | 0.24242 | 0.2425 | 0.24258 | 0.24267 | 0.24275 | 0.24283 | 0.24291 | 0.243 | 0.24308 | 0.24316 | 0.24442
77 | 0.24035 | 0.24043 | 0.24051 | 0.24059 | 0.24067 | 0.24075 | 0.24083 | 0.24092 | 0.241 | 0.24108 | 0.24116 | 0.24124 | 0.24133 | 0.24141 | 0.24149 | 0.24157 | 0.24166 | 0.24174 | 0.24182 | 0.24191 | 0.24199 | 0.24208 | 0.24216 | 0.24224 | 0.24233 | 0.24241 | 0.2425 | 0.24258 | 0.24267 | 0.24275 | 0.24284 | 0.24292 | 0.24301 | 0.24309 | 0.24318 | 0.24326 | 0.24457
78 | 0.24035 | 0.24044 | 0.24052 | 0.2406 | 0.24069 | 0.24077 | 0.24086 | 0.24094 | 0.24102 | 0.24111 | 0.24119 | 0.24128 | 0.24136 | 0.24145 | 0.24154 | 0.24162 | 0.24171 | 0.24179 | 0.24188 | 0.24197 | 0.24205 | 0.24214 | 0.24223 | 0.24231 | 0.2424 | 0.24249 | 0.24257 | 0.24266 | 0.24275 | 0.24284 | 0.24293 | 0.24301 | 0.2431 | 0.24319 | 0.24328 | 0.24337 | 0.24472
79 | 0.24036 | 0.24044 | 0.24053 | 0.24062 | 0.2407 | 0.24079 | 0.24088 | 0.24096 | 0.24105 | 0.24114 | 0.24123 | 0.24132 | 0.2414 | 0.24149 | 0.24158 | 0.24167 | 0.24176 | 0.24185 | 0.24194 | 0.24203 | 0.24211 | 0.2422 | 0.24229 | 0.24238 | 0.24247 | 0.24256 | 0.24265 | 0.24275 | 0.24284 | 0.24293 | 0.24302 | 0.24311 | 0.2432 | 0.24329 | 0.24339 | 0.24348 | 0.24488
80 | 0.24036 | 0.24045 | 0.24054 | 0.24063 | 0.24072 | 0.24081 | 0.2409 | 0.24099 | 0.24108 | 0.24117 | 0.24126 | 0.24135 | 0.24144 | 0.24153 | 0.24163 | 0.24172 | 0.24181 | 0.2419 | 0.24199 | 0.24209 | 0.24218 | 0.24227 | 0.24236 | 0.24246 | 0.24255 | 0.24264 | 0.24274 | 0.24283 | 0.24293 | 0.24302 | 0.24311 | 0.24321 | 0.2433 | 0.2434 | 0.24349 | 0.24359 | 0.24504
81 | 0.24037 | 0.24046 | 0.24055 | 0.24064 | 0.24074 | 0.24083 | 0.24092 | 0.24102 | 0.24111 | 0.2412 | 0.2413 | 0.24139 | 0.24148 | 0.24158 | 0.24167 | 0.24177 | 0.24186 | 0.24196 | 0.24205 | 0.24215 | 0.24224 | 0.24234 | 0.24244 | 0.24253 | 0.24263 | 0.24273 | 0.24282 | 0.24292 | 0.24302 | 0.24311 | 0.24321 | 0.24331 | 0.24341 | 0.24351 | 0.2436 | 0.2437 | 0.2452
82 | 0.24037 | 0.24047 | 0.24056 | 0.24066 | 0.24075 | 0.24085 | 0.24095 | 0.24104 | 0.24114 | 0.24124 | 0.24133 | 0.24143 | 0.24153 | 0.24162 | 0.24172 | 0.24182 | 0.24192 | 0.24202 | 0.24212 | 0.24221 | 0.24231 | 0.24241 | 0.24251 | 0.24261 | 0.24271 | 0.24281 | 0.24291 | 0.24301 | 0.24311 | 0.24321 | 0.24331 | 0.24341 | 0.24352 | 0.24362 | 0.24372 | 0.24382 | 0.24538
83 | 0.24038 | 0.24048 | 0.24057 | 0.24067 | 0.24077 | 0.24087 | 0.24097 | 0.24107 | 0.24117 | 0.24127 | 0.24137 | 0.24147 | 0.24157 | 0.24167 | 0.24177 | 0.24187 | 0.24197 | 0.24208 | 0.24218 | 0.24228 | 0.24238 | 0.24249 | 0.24259 | 0.24269 | 0.24279 | 0.2429 | 0.243 | 0.2431 | 0.24321 | 0.24331 | 0.24342 | 0.24352 | 0.24363 | 0.24373 | 0.24384 | 0.24394 | 0.24555
84 | 0.24038 | 0.24048 | 0.24059 | 0.24069 | 0.24079 | 0.24089 | 0.24099 | 0.2411 | 0.2412 | 0.2413 | 0.24141 | 0.24151 | 0.24161 | 0.24172 | 0.24182 | 0.24193 | 0.24203 | 0.24214 | 0.24224 | 0.24235 | 0.24245 | 0.24256 | 0.24267 | 0.24277 | 0.24288 | 0.24299 | 0.24309 | 0.2432 | 0.24331 | 0.24342 | 0.24352 | 0.24363 | 0.24374 | 0.24385 | 0.24396 | 0.24407 | 0.24573
85 | 0.24039 | 0.24049 | 0.2406 | 0.2407 | 0.24081 | 0.24091 | 0.24102 | 0.24113 | 0.24123 | 0.24134 | 0.24145 | 0.24155 | 0.24166 | 0.24177 | 0.24188 | 0.24198 | 0.24209 | 0.2422 | 0.24231 | 0.24242 | 0.24253 | 0.24264 | 0.24275 | 0.24286 | 0.24297 | 0.24308 | 0.24319 | 0.2433 | 0.24341 | 0.24352 | 0.24363 | 0.24375 | 0.24386 | 0.24397 | 0.24408 | 0.2442 | 0.24592
86 | 0.24039 | 0.2405 | 0.24061 | 0.24072 | 0.24083 | 0.24094 | 0.24105 | 0.24116 | 0.24127 | 0.24138 | 0.24149 | 0.2416 | 0.24171 | 0.24182 | 0.24193 | 0.24204 | 0.24215 | 0.24227 | 0.24238 | 0.24249 | 0.2426 | 0.24272 | 0.24283 | 0.24294 | 0.24306 | 0.24317 | 0.24329 | 0.2434 | 0.24352 | 0.24363 | 0.24375 | 0.24386 | 0.24398 | 0.2441 | 0.24421 | 0.24433 | 0.24611
87 | 0.2404 | 0.24051 | 0.24062 | 0.24073 | 0.24085 | 0.24096 | 0.24107 | 0.24119 | 0.2413 | 0.24141 | 0.24153 | 0.24164 | 0.24176 | 0.24187 | 0.24199 | 0.2421 | 0.24222 | 0.24233 | 0.24245 | 0.24257 | 0.24268 | 0.2428 | 0.24292 | 0.24303 | 0.24315 | 0.24327 | 0.24339 | 0.24351 | 0.24363 | 0.24374 | 0.24386 | 0.24398 | 0.2441 | 0.24422 | 0.24434 | 0.24447 | 0.24631
88 | 0.2404 | 0.24052 | 0.24063 | 0.24075 | 0.24087 | 0.24098 | 0.2411 | 0.24122 | 0.24133 | 0.24145 | 0.24157 | 0.24169 | 0.24181 | 0.24192 | 0.24204 | 0.24216 | 0.24228 | 0.2424 | 0.24252 | 0.24264 | 0.24276 | 0.24288 | 0.243 | 0.24313 | 0.24325 | 0.24337 | 0.24349 | 0.24361 | 0.24374 | 0.24386 | 0.24398 | 0.24411 | 0.24423 | 0.24436 | 0.24448 | 0.24461 | 0.24651
89 | 0.24041 | 0.24053 | 0.24065 | 0.24077 | 0.24089 | 0.24101 | 0.24113 | 0.24125 | 0.24137 | 0.24149 | 0.24161 | 0.24173 | 0.24186 | 0.24198 | 0.2421 | 0.24223 | 0.24235 | 0.24247 | 0.2426 | 0.24272 | 0.24285 | 0.24297 | 0.2431 | 0.24322 | 0.24335 | 0.24347 | 0.2436 | 0.24373 | 0.24385 | 0.24398 | 0.24411 | 0.24424 | 0.24436 | 0.24449 | 0.24462 | 0.24475 | 0.24672
90 | 0.24041 | 0.24054 | 0.24066 | 0.24078 | 0.24091 | 0.24103 | 0.24116 | 0.24128 | 0.24141 | 0.24153 | 0.24166 | 0.24178 | 0.24191 | 0.24204 | 0.24216 | 0.24229 | 0.24242 | 0.24254 | 0.24267 | 0.2428 | 0.24293 | 0.24306 | 0.24319 | 0.24332 | 0.24345 | 0.24358 | 0.24371 | 0.24384 | 0.24397 | 0.2441 | 0.24423 | 0.24437 | 0.2445 | 0.24463 | 0.24476 | 0.2449 | 0.24694
91 | 0.24042 | 0.24055 | 0.24067 | 0.2408 | 0.24093 | 0.24106 | 0.24118 | 0.24131 | 0.24144 | 0.24157 | 0.2417 | 0.24183 | 0.24196 | 0.24209 | 0.24222 | 0.24236 | 0.24249 | 0.24262 | 0.24275 | 0.24288 | 0.24302 | 0.24315 | 0.24328 | 0.24342 | 0.24355 | 0.24369 | 0.24382 | 0.24396 | 0.24409 | 0.24423 | 0.24436 | 0.2445 | 0.24464 | 0.24478 | 0.24491 | 0.24505 | 0.24716
92 | 0.24042 | 0.24056 | 0.24069 | 0.24082 | 0.24095 | 0.24108 | 0.24121 | 0.24135 | 0.24148 | 0.24161 | 0.24175 | 0.24188 | 0.24202 | 0.24215 | 0.24229 | 0.24242 | 0.24256 | 0.2427 | 0.24283 | 0.24297 | 0.24311 | 0.24324 | 0.24338 | 0.24352 | 0.24366 | 0.2438 | 0.24394 | 0.24408 | 0.24422 | 0.24436 | 0.2445 | 0.24464 | 0.24478 | 0.24492 | 0.24507 | 0.24521 | 0.24739
93 | 0.24043 | 0.24056 | 0.2407 | 0.24084 | 0.24097 | 0.24111 | 0.24125 | 0.24138 | 0.24152 | 0.24166 | 0.2418 | 0.24193 | 0.24207 | 0.24221 | 0.24235 | 0.24249 | 0.24263 | 0.24277 | 0.24292 | 0.24306 | 0.2432 | 0.24334 | 0.24348 | 0.24363 | 0.24377 | 0.24391 | 0.24406 | 0.2442 | 0.24435 | 0.24449 | 0.24464 | 0.24478 | 0.24493 | 0.24508 | 0.24522 | 0.24537 | 0.24762
94 | 0.24044 | 0.24057 | 0.24071 | 0.24085 | 0.24099 | 0.24114 | 0.24128 | 0.24142 | 0.24156 | 0.2417 | 0.24185 | 0.24199 | 0.24213 | 0.24228 | 0.24242 | 0.24256 | 0.24271 | 0.24285 | 0.243 | 0.24315 | 0.24329 | 0.24344 | 0.24359 | 0.24373 | 0.24388 | 0.24403 | 0.24418 | 0.24433 | 0.24448 | 0.24463 | 0.24478 | 0.24493 | 0.24508 | 0.24523 | 0.24538 | 0.24554 | 0.24787
95 | 0.24044 | 0.24058 | 0.24073 | 0.24087 | 0.24102 | 0.24116 | 0.24131 | 0.24146 | 0.2416 | 0.24175 | 0.2419 | 0.24204 | 0.24219 | 0.24234 | 0.24249 | 0.24264 | 0.24279 | 0.24294 | 0.24309 | 0.24324 | 0.24339 | 0.24354 | 0.24369 | 0.24385 | 0.244 | 0.24415 | 0.24431 | 0.24446 | 0.24461 | 0.24477 | 0.24492 | 0.24508 | 0.24524 | 0.24539 | 0.24555 | 0.24571 | 0.24812
96 | 0.24045 | 0.24059 | 0.24074 | 0.24089 | 0.24104 | 0.24119 | 0.24134 | 0.24149 | 0.24164 | 0.2418 | 0.24195 | 0.2421 | 0.24225 | 0.24241 | 0.24256 | 0.24271 | 0.24287 | 0.24302 | 0.24318 | 0.24333 | 0.24349 | 0.24365 | 0.2438 | 0.24396 | 0.24412 | 0.24428 | 0.24443 | 0.24459 | 0.24475 | 0.24491 | 0.24507 | 0.24523 | 0.2454 | 0.24556 | 0.24572 | 0.24588 | 0.24837
97 | 0.24045 | 0.24061 | 0.24076 | 0.24091 | 0.24107 | 0.24122 | 0.24138 | 0.24153 | 0.24169 | 0.24184 | 0.242 | 0.24216 | 0.24232 | 0.24247 | 0.24263 | 0.24279 | 0.24295 | 0.24311 | 0.24327 | 0.24343 | 0.24359 | 0.24375 | 0.24392 | 0.24408 | 0.24424 | 0.2444 | 0.24457 | 0.24473 | 0.2449 | 0.24506 | 0.24523 | 0.24539 | 0.24556 | 0.24573 | 0.24589 | 0.24606 | 0.24864
98 | 0.24046 | 0.24062 | 0.24077 | 0.24093 | 0.24109 | 0.24125 | 0.24141 | 0.24157 | 0.24173 | 0.24189 | 0.24205 | 0.24222 | 0.24238 | 0.24254 | 0.24271 | 0.24287 | 0.24303 | 0.2432 | 0.24336 | 0.24353 | 0.2437 | 0.24386 | 0.24403 | 0.2442 | 0.24437 | 0.24454 | 0.2447 | 0.24487 | 0.24504 | 0.24521 | 0.24539 | 0.24556 | 0.24573 | 0.2459 | 0.24607 | 0.24625 | 0.24891
99 | 0.24046 | 0.24063 | 0.24079 | 0.24095 | 0.24112 | 0.24128 | 0.24145 | 0.24161 | 0.24178 | 0.24194 | 0.24211 | 0.24228 | 0.24245 | 0.24261 | 0.24278 | 0.24295 | 0.24312 | 0.24329 | 0.24346 | 0.24363 | 0.2438 | 0.24398 | 0.24415 | 0.24432 | 0.2445 | 0.24467 | 0.24484 | 0.24502 | 0.2452 | 0.24537 | 0.24555 | 0.24573 | 0.2459 | 0.24608 | 0.24626 | 0.24644 | 0.24919
100 | 0.24047 | 0.24064 | 0.24081 | 0.24097 | 0.24114 | 0.24131 | 0.24148 | 0.24165 | 0.24182 | 0.242 | 0.24217 | 0.24234 | 0.24251 | 0.24269 | 0.24286 | 0.24303 | 0.24321 | 0.24339 | 0.24356 | 0.24374 | 0.24392 | 0.24409 | 0.24427 | 0.24445 | 0.24463 | 0.24481 | 0.24499 | 0.24517 | 0.24535 | 0.24553 | 0.24572 | 0.2459 | 0.24608 | 0.24627 | 0.24645 | 0.24664 | 0.24948
101 | 0.24048 | 0.24065 | 0.24082 | 0.241 | 0.24117 | 0.24134 | 0.24152 | 0.2417 | 0.24187 | 0.24205 | 0.24223 | 0.2424 | 0.24258 | 0.24276 | 0.24294 | 0.24312 | 0.2433 | 0.24348 | 0.24366 | 0.24385 | 0.24403 | 0.24421 | 0.2444 | 0.24458 | 0.24477 | 0.24495 | 0.24514 | 0.24532 | 0.24551 | 0.2457 | 0.24589 | 0.24608 | 0.24627 | 0.24646 | 0.24665 | 0.24684 | 0.24977
102 | 0.24048 | 0.24066 | 0.24084 | 0.24102 | 0.2412 | 0.24138 | 0.24156 | 0.24174 | 0.24192 | 0.2421 | 0.24229 | 0.24247 | 0.24265 | 0.24284 | 0.24302 | 0.24321 | 0.2434 | 0.24358 | 0.24377 | 0.24396 | 0.24415 | 0.24433 | 0.24452 | 0.24471 | 0.24491 | 0.2451 | 0.24529 | 0.24548 | 0.24568 | 0.24587 | 0.24606 | 0.24626 | 0.24645 | 0.24665 | 0.24685 | 0.24704 | 0.25008
103 | 0.24049 | 0.24067 | 0.24086 | 0.24104 | 0.24122 | 0.24141 | 0.2416 | 0.24178 | 0.24197 | 0.24216 | 0.24235 | 0.24254 | 0.24273 | 0.24292 | 0.24311 | 0.2433 | 0.24349 | 0.24368 | 0.24388 | 0.24407 | 0.24427 | 0.24446 | 0.24466 | 0.24485 | 0.24505 | 0.24525 | 0.24545 | 0.24564 | 0.24584 | 0.24604 | 0.24624 | 0.24645 | 0.24665 | 0.24685 | 0.24705 | 0.24726 | 0.25039
104 | 0.24049 | 0.24068 | 0.24087 | 0.24106 | 0.24125 | 0.24144 | 0.24164 | 0.24183 | 0.24202 | 0.24222 | 0.24241 | 0.24261 | 0.2428 | 0.243 | 0.24319 | 0.24339 | 0.24359 | 0.24379 | 0.24399 | 0.24419 | 0.24439 | 0.24459 | 0.24479 | 0.24499 | 0.2452 | 0.2454 | 0.24561 | 0.24581 | 0.24602 | 0.24622 | 0.24643 | 0.24664 | 0.24685 | 0.24706 | 0.24727 | 0.24748 | 0.25071
105 | 0.2405 | 0.2407 | 0.24089 | 0.24109 | 0.24128 | 0.24148 | 0.24168 | 0.24188 | 0.24208 | 0.24227 | 0.24248 | 0.24268 | 0.24288 | 0.24308 | 0.24328 | 0.24349 | 0.24369 | 0.2439 | 0.2441 | 0.24431 | 0.24451 | 0.24472 | 0.24493 | 0.24514 | 0.24535 | 0.24556 | 0.24577 | 0.24598 | 0.24619 | 0.24641 | 0.24662 | 0.24684 | 0.24705 | 0.24727 | 0.24748 | 0.2477 | 0.25104
106 | 0.24051 | 0.24071 | 0.24091 | 0.24111 | 0.24131 | 0.24152 | 0.24172 | 0.24192 | 0.24213 | 0.24233 | 0.24254 | 0.24275 | 0.24296 | 0.24317 | 0.24337 | 0.24358 | 0.24379 | 0.24401 | 0.24422 | 0.24443 | 0.24464 | 0.24486 | 0.24507 | 0.24529 | 0.24551 | 0.24572 | 0.24594 | 0.24616 | 0.24638 | 0.2466 | 0.24682 | 0.24704 | 0.24726 | 0.24748 | 0.24771 | 0.24793 | 0.25138
107 | 0.24051 | 0.24072 | 0.24093 | 0.24113 | 0.24134 | 0.24155 | 0.24176 | 0.24197 | 0.24218 | 0.2424 | 0.24261 | 0.24282 | 0.24304 | 0.24325 | 0.24347 | 0.24368 | 0.2439 | 0.24412 | 0.24434 | 0.24456 | 0.24478 | 0.245 | 0.24522 | 0.24544 | 0.24567 | 0.24589 | 0.24611 | 0.24634 | 0.24657 | 0.24679 | 0.24702 | 0.24725 | 0.24748 | 0.24771 | 0.24794 | 0.24817 | 0.25173
108 | 0.24052 | 0.24073 | 0.24095 | 0.24116 | 0.24137 | 0.24159 | 0.24181 | 0.24202 | 0.24224 | 0.24246 | 0.24268 | 0.2429 | 0.24312 | 0.24334 | 0.24356 | 0.24379 | 0.24401 | 0.24424 | 0.24446 | 0.24469 | 0.24491 | 0.24514 | 0.24537 | 0.2456 | 0.24583 | 0.24606 | 0.24629 | 0.24652 | 0.24676 | 0.24699 | 0.24723 | 0.24746 | 0.2477 | 0.24794 | 0.24817 | 0.24841 | 0.25209
109 | 0.24053 | 0.24075 | 0.24096 | 0.24119 | 0.24141 | 0.24163 | 0.24185 | 0.24207 | 0.2423 | 0.24252 | 0.24275 | 0.24298 | 0.2432 | 0.24343 | 0.24366 | 0.24389 | 0.24412 | 0.24435 | 0.24459 | 0.24482 | 0.24505 | 0.24529 | 0.24552 | 0.24576 | 0.246 | 0.24624 | 0.24648 | 0.24672 | 0.24696 | 0.2472 | 0.24744 | 0.24768 | 0.24793 | 0.24817 | 0.24842 | 0.24866 | 0.25247
110 | 0.24053 | 0.24076 | 0.24098 | 0.24121 | 0.24144 | 0.24167 | 0.2419 | 0.24213 | 0.24236 | 0.24259 | 0.24282 | 0.24306 | 0.24329 | 0.24353 | 0.24376 | 0.244 | 0.24424 | 0.24448 | 0.24472 | 0.24496 | 0.2452 | 0.24544 | 0.24568 | 0.24593 | 0.24617 | 0.24642 | 0.24666 | 0.24691 | 0.24716 | 0.24741 | 0.24766 | 0.24791 | 0.24816 | 0.24841 | 0.24867 | 0.24892 | 0.25285
111 | 0.24054 | 0.24077 | 0.241 | 0.24124 | 0.24147 | 0.24171 | 0.24194 | 0.24218 | 0.24242 | 0.24266 | 0.2429 | 0.24314 | 0.24338 | 0.24362 | 0.24387 | 0.24411 | 0.24436 | 0.2446 | 0.24485 | 0.2451 | 0.24534 | 0.24559 | 0.24585 | 0.2461 | 0.24635 | 0.2466 | 0.24686 | 0.24711 | 0.24737 | 0.24762 | 0.24788 | 0.24814 | 0.2484 | 0.24866 | 0.24892 | 0.24919 | 0.25324
Dry and Saturated values check exactly to ASHRAE Fundamentals Table 2
For comparison -- Isochoric specific heat from cv_ptW_HAP_IP -- for comparison only -- ISOBARIC value is what to use in local atmosphere -- isobaric recognizes that there is pressure volume work being done and so is greater
Relative Humidity
Temperature F | 0% | 2% | 4% | 6% | 8% | 10% | 12% | 14% | 16% | 18% | 20% | 22% | 24% | 26% | 28% | 30% | 32% | 34% | 36% | 38% | 40% | 42% | 44% | 46% | 48% | 50% | 52% | 54% | 56% | 58% | 60% | 62% | 64% | 66% | 68% | 70% | 100%
55 | 0.17134 | 0.17137 | 0.1714 | 0.17143 | 0.17146 | 0.17149 | 0.17152 | 0.17155 | 0.17158 | 0.17161 | 0.17164 | 0.17167 | 0.1717 | 0.17173 | 0.17176 | 0.17179 | 0.17182 | 0.17185 | 0.17188 | 0.17191 | 0.17194 | 0.17197 | 0.172 | 0.17203 | 0.17206 | 0.17209 | 0.17212 | 0.17216 | 0.17219 | 0.17222 | 0.17225 | 0.17228 | 0.17231 | 0.17234 | 0.17237 | 0.1724 | 0.17287
56 | 0.17134 | 0.17138 | 0.17141 | 0.17144 | 0.17147 | 0.1715 | 0.17153 | 0.17156 | 0.17159 | 0.17162 | 0.17166 | 0.17169 | 0.17172 | 0.17175 | 0.17178 | 0.17181 | 0.17184 | 0.17187 | 0.17191 | 0.17194 | 0.17197 | 0.172 | 0.17203 | 0.17206 | 0.1721 | 0.17213 | 0.17216 | 0.17219 | 0.17222 | 0.17225 | 0.17229 | 0.17232 | 0.17235 | 0.17238 | 0.17241 | 0.17245 | 0.17293
57 | 0.17135 | 0.17138 | 0.17141 | 0.17145 | 0.17148 | 0.17151 | 0.17154 | 0.17157 | 0.17161 | 0.17164 | 0.17167 | 0.1717 | 0.17174 | 0.17177 | 0.1718 | 0.17183 | 0.17187 | 0.1719 | 0.17193 | 0.17196 | 0.172 | 0.17203 | 0.17206 | 0.1721 | 0.17213 | 0.17216 | 0.17219 | 0.17223 | 0.17226 | 0.17229 | 0.17233 | 0.17236 | 0.17239 | 0.17243 | 0.17246 | 0.17249 | 0.173
58 | 0.17136 | 0.17139 | 0.17142 | 0.17145 | 0.17149 | 0.17152 | 0.17155 | 0.17159 | 0.17162 | 0.17166 | 0.17169 | 0.17172 | 0.17176 | 0.17179 | 0.17182 | 0.17186 | 0.17189 | 0.17192 | 0.17196 | 0.17199 | 0.17203 | 0.17206 | 0.17209 | 0.17213 | 0.17216 | 0.1722 | 0.17223 | 0.17227 | 0.1723 | 0.17233 | 0.17237 | 0.1724 | 0.17244 | 0.17247 | 0.17251 | 0.17254 | 0.17306
59 | 0.17136 | 0.17139 | 0.17143 | 0.17146 | 0.1715 | 0.17153 | 0.17157 | 0.1716 | 0.17164 | 0.17167 | 0.17171 | 0.17174 | 0.17178 | 0.17181 | 0.17185 | 0.17188 | 0.17192 | 0.17195 | 0.17199 | 0.17202 | 0.17206 | 0.17209 | 0.17213 | 0.17216 | 0.1722 | 0.17223 | 0.17227 | 0.1723 | 0.17234 | 0.17238 | 0.17241 | 0.17245 | 0.17248 | 0.17252 | 0.17255 | 0.17259 | 0.17313
60 | 0.17137 | 0.1714 | 0.17144 | 0.17147 | 0.17151 | 0.17154 | 0.17158 | 0.17162 | 0.17165 | 0.17169 | 0.17172 | 0.17176 | 0.1718 | 0.17183 | 0.17187 | 0.17191 | 0.17194 | 0.17198 | 0.17201 | 0.17205 | 0.17209 | 0.17212 | 0.17216 | 0.1722 | 0.17223 | 0.17227 | 0.17231 | 0.17234 | 0.17238 | 0.17242 | 0.17245 | 0.17249 | 0.17253 | 0.17257 | 0.1726 | 0.17264 | 0.1732
61 | 0.17137 | 0.17141 | 0.17144 | 0.17148 | 0.17152 | 0.17156 | 0.17159 | 0.17163 | 0.17167 | 0.17171 | 0.17174 | 0.17178 | 0.17182 | 0.17185 | 0.17189 | 0.17193 | 0.17197 | 0.17201 | 0.17204 | 0.17208 | 0.17212 | 0.17216 | 0.17219 | 0.17223 | 0.17227 | 0.17231 | 0.17235 | 0.17239 | 0.17242 | 0.17246 | 0.1725 | 0.17254 | 0.17258 | 0.17262 | 0.17265 | 0.17269 | 0.17328
62 | 0.17138 | 0.17141 | 0.17145 | 0.17149 | 0.17153 | 0.17157 | 0.17161 | 0.17165 | 0.17168 | 0.17172 | 0.17176 | 0.1718 | 0.17184 | 0.17188 | 0.17192 | 0.17196 | 0.17199 | 0.17203 | 0.17207 | 0.17211 | 0.17215 | 0.17219 | 0.17223 | 0.17227 | 0.17231 | 0.17235 | 0.17239 | 0.17243 | 0.17247 | 0.17251 | 0.17255 | 0.17259 | 0.17263 | 0.17267 | 0.17271 | 0.17275 | 0.17335
63 | 0.17138 | 0.17142 | 0.17146 | 0.1715 | 0.17154 | 0.17158 | 0.17162 | 0.17166 | 0.1717 | 0.17174 | 0.17178 | 0.17182 | 0.17186 | 0.1719 | 0.17194 | 0.17198 | 0.17202 | 0.17206 | 0.1721 | 0.17214 | 0.17219 | 0.17223 | 0.17227 | 0.17231 | 0.17235 | 0.17239 | 0.17243 | 0.17247 | 0.17251 | 0.17255 | 0.17259 | 0.17264 | 0.17268 | 0.17272 | 0.17276 | 0.1728 | 0.17343
64 | 0.17139 | 0.17143 | 0.17147 | 0.17151 | 0.17155 | 0.17159 | 0.17163 | 0.17168 | 0.17172 | 0.17176 | 0.1718 | 0.17184 | 0.17188 | 0.17193 | 0.17197 | 0.17201 | 0.17205 | 0.17209 | 0.17214 | 0.17218 | 0.17222 | 0.17226 | 0.1723 | 0.17235 | 0.17239 | 0.17243 | 0.17247 | 0.17252 | 0.17256 | 0.1726 | 0.17264 | 0.17269 | 0.17273 | 0.17277 | 0.17282 | 0.17286 | 0.17351
65 | 0.17139 | 0.17143 | 0.17148 | 0.17152 | 0.17156 | 0.17161 | 0.17165 | 0.17169 | 0.17173 | 0.17178 | 0.17182 | 0.17186 | 0.17191 | 0.17195 | 0.17199 | 0.17204 | 0.17208 | 0.17212 | 0.17217 | 0.17221 | 0.17225 | 0.1723 | 0.17234 | 0.17239 | 0.17243 | 0.17247 | 0.17252 | 0.17256 | 0.17261 | 0.17265 | 0.1727 | 0.17274 | 0.17278 | 0.17283 | 0.17287 | 0.17292 | 0.17359
66 | 0.1714 | 0.17144 | 0.17149 | 0.17153 | 0.17157 | 0.17162 | 0.17166 | 0.17171 | 0.17175 | 0.1718 | 0.17184 | 0.17189 | 0.17193 | 0.17198 | 0.17202 | 0.17207 | 0.17211 | 0.17216 | 0.1722 | 0.17225 | 0.17229 | 0.17234 | 0.17238 | 0.17243 | 0.17247 | 0.17252 | 0.17256 | 0.17261 | 0.17266 | 0.1727 | 0.17275 | 0.17279 | 0.17284 | 0.17289 | 0.17293 | 0.17298 | 0.17368
67 | 0.1714 | 0.17145 | 0.17149 | 0.17154 | 0.17159 | 0.17163 | 0.17168 | 0.17172 | 0.17177 | 0.17182 | 0.17186 | 0.17191 | 0.17196 | 0.172 | 0.17205 | 0.1721 | 0.17214 | 0.17219 | 0.17224 | 0.17228 | 0.17233 | 0.17238 | 0.17242 | 0.17247 | 0.17252 | 0.17256 | 0.17261 | 0.17266 | 0.17271 | 0.17275 | 0.1728 | 0.17285 | 0.1729 | 0.17294 | 0.17299 | 0.17304 | 0.17377
68 | 0.17141 | 0.17146 | 0.1715 | 0.17155 | 0.1716 | 0.17165 | 0.17169 | 0.17174 | 0.17179 | 0.17184 | 0.17188 | 0.17193 | 0.17198 | 0.17203 | 0.17208 | 0.17213 | 0.17217 | 0.17222 | 0.17227 | 0.17232 | 0.17237 | 0.17242 | 0.17246 | 0.17251 | 0.17256 | 0.17261 | 0.17266 | 0.17271 | 0.17276 | 0.17281 | 0.17286 | 0.17291 | 0.17296 | 0.17301 | 0.17306 | 0.1731 | 0.17386
69 | 0.17141 | 0.17146 | 0.17151 | 0.17156 | 0.17161 | 0.17166 | 0.17171 | 0.17176 | 0.17181 | 0.17186 | 0.17191 | 0.17196 | 0.17201 | 0.17206 | 0.17211 | 0.17216 | 0.17221 | 0.17226 | 0.17231 | 0.17236 | 0.17241 | 0.17246 | 0.17251 | 0.17256 | 0.17261 | 0.17266 | 0.17271 | 0.17276 | 0.17281 | 0.17286 | 0.17291 | 0.17297 | 0.17302 | 0.17307 | 0.17312 | 0.17317 | 0.17395
70 | 0.17142 | 0.17147 | 0.17152 | 0.17157 | 0.17162 | 0.17167 | 0.17173 | 0.17178 | 0.17183 | 0.17188 | 0.17193 | 0.17198 | 0.17203 | 0.17208 | 0.17214 | 0.17219 | 0.17224 | 0.17229 | 0.17234 | 0.1724 | 0.17245 | 0.1725 | 0.17255 | 0.1726 | 0.17266 | 0.17271 | 0.17276 | 0.17281 | 0.17287 | 0.17292 | 0.17297 | 0.17303 | 0.17308 | 0.17313 | 0.17319 | 0.17324 | 0.17405
71 | 0.17143 | 0.17148 | 0.17153 | 0.17158 | 0.17164 | 0.17169 | 0.17174 | 0.17179 | 0.17185 | 0.1719 | 0.17195 | 0.17201 | 0.17206 | 0.17211 | 0.17217 | 0.17222 | 0.17227 | 0.17233 | 0.17238 | 0.17244 | 0.17249 | 0.17254 | 0.1726 | 0.17265 | 0.17271 | 0.17276 | 0.17282 | 0.17287 | 0.17292 | 0.17298 | 0.17303 | 0.17309 | 0.17314 | 0.1732 | 0.17325 | 0.17331 | 0.17415
72 | 0.17143 | 0.17149 | 0.17154 | 0.17159 | 0.17165 | 0.1717 | 0.17176 | 0.17181 | 0.17187 | 0.17192 | 0.17198 | 0.17203 | 0.17209 | 0.17214 | 0.1722 | 0.17225 | 0.17231 | 0.17237 | 0.17242 | 0.17248 | 0.17253 | 0.17259 | 0.17264 | 0.1727 | 0.17276 | 0.17281 | 0.17287 | 0.17293 | 0.17298 | 0.17304 | 0.1731 | 0.17315 | 0.17321 | 0.17327 | 0.17332 | 0.17338 | 0.17425
73 | 0.17144 | 0.17149 | 0.17155 | 0.17161 | 0.17166 | 0.17172 | 0.17178 | 0.17183 | 0.17189 | 0.17195 | 0.172 | 0.17206 | 0.17212 | 0.17217 | 0.17223 | 0.17229 | 0.17235 | 0.1724 | 0.17246 | 0.17252 | 0.17258 | 0.17263 | 0.17269 | 0.17275 | 0.17281 | 0.17287 | 0.17293 | 0.17298 | 0.17304 | 0.1731 | 0.17316 | 0.17322 | 0.17328 | 0.17334 | 0.1734 | 0.17346 | 0.17436
74 | 0.17144 | 0.1715 | 0.17156 | 0.17162 | 0.17168 | 0.17173 | 0.17179 | 0.17185 | 0.17191 | 0.17197 | 0.17203 | 0.17209 | 0.17215 | 0.17221 | 0.17226 | 0.17232 | 0.17238 | 0.17244 | 0.1725 | 0.17256 | 0.17262 | 0.17268 | 0.17274 | 0.1728 | 0.17286 | 0.17292 | 0.17298 | 0.17304 | 0.1731 | 0.17317 | 0.17323 | 0.17329 | 0.17335 | 0.17341 | 0.17347 | 0.17353 | 0.17446
75 | 0.17145 | 0.17151 | 0.17157 | 0.17163 | 0.17169 | 0.17175 | 0.17181 | 0.17187 | 0.17193 | 0.17199 | 0.17205 | 0.17212 | 0.17218 | 0.17224 | 0.1723 | 0.17236 | 0.17242 | 0.17248 | 0.17255 | 0.17261 | 0.17267 | 0.17273 | 0.17279 | 0.17286 | 0.17292 | 0.17298 | 0.17304 | 0.17311 | 0.17317 | 0.17323 | 0.17329 | 0.17336 | 0.17342 | 0.17348 | 0.17355 | 0.17361 | 0.17458

## Heat flow
Testing consistency of moisture content before and after flow through heat pump
[13 empty] | Verification round trip for W | [5 empty] | Air specific Enthalpy in BTU/lbdryair, using h_ptW_HAP_IP
Reading time | Reading Pump | Temp In | Temp Out | RH In | RH Out | W in | W out | Mass Moisture Fraction In | Mass Moisture Fraction Out | Barometer mb | Barometer PSI | Mass Moisture Fraction out/in | Temp In C | Temp out C | H in from W | H out from W | Check Sum to 5 dec |  | H in | H out | H hybrid (T out with W in) | Delta H | Delta H hybr | Specific Heat In | Specific heat x temp gain | Gain by specific heat vs enthalpy change
645AM Jan 7 | Downstairs | 64.66 | 109.6 | 34.03 | 9.17 | 0.004401 | 0.0049609 | 0.0043816 | 0.0049363 | 1013.25 | 14.6959 | 11.24% | 18.1444 | 43.1111 | 34.03 | 9.17 | 3.6863e-06 | 9.9366e-07 | 20.3261 | 31.8397 | 31.2185 | 11.5136 | 10.8924 | 0.24121 | 10.8399 | -0.4822%
900 AM Jan 7 | Downstairs | 65.3 | 98.4 | 35.33 | 12.83 | 0.0046742 | 0.0049799 | 0.0046524 | 0.0049551 | 1013.25 | 14.6959 | 6.108% | 18.5 | 36.8889 | 35.33 | 12.83 | 3.8271e-06 | 1.3902e-06 | 20.7789 | 29.1422 | 28.8047 | 8.3633 | 8.0258 | 0.24127 | 7.9859 | -0.4962%
8AM Jan 7 | Downstairs | 66.1 | 108 | 34.05 | 9.77 | 0.0046316 | 0.0050459 | 0.0046102 | 0.0050204 | 1013.25 | 14.6959 | 8.172% | 18.9444 | 42.2222 | 34.05 | 9.77 | 3.6885e-06 | 1.0587e-06 | 20.9264 | 31.5455 | 31.0863 | 10.6191 | 10.1599 | 0.24126 | 10.1088 | -0.5022%
2:00P Jan 6 | Downstairs | 67.6 | 103.4 | 28.96 | 9.92 | 0.0041458 | 0.0044703 | 0.0041287 | 0.0044503 | 1013.25 | 14.6959 | 7.227% | 19.7778 | 39.6667 | 28.96 | 9.92 | 3.1372e-06 | 1.0749e-06 | 20.7602 | 29.7918 | 29.4328 | 9.0316 | 8.6726 | 0.24117 | 8.6337 | -0.4479%
6AM, Jan 7 | Upstairs | 67.65 | 85.97 | 43.24 | 24.7 | 0.0062214 | 0.0065286 | 0.0061827 | 0.006486 | 1013.25 | 14.6959 | 4.677% | 19.8056 | 29.9833 | 43.24 | 24.7 | 4.6841e-06 | 2.6762e-06 | 23.0357 | 27.8276 | 27.49 | 4.7919 | 4.4543 | 0.2416 | 4.4261 | -0.6344%
12:39P Jan 6 | Upstairs | 70.6 | 90.9 | 37.2 | 21.3 | 0.0059187 | 0.0065792 | 0.0058837 | 0.006536 | 1013.25 | 14.6959 | 9.98% | 21.4444 | 32.7222 | 37.2 | 21.3 | 4.03e-06 | 2.3079e-06 | 23.4224 | 29.083 | 28.3557 | 5.6606 | 4.9334 | 0.24155 | 4.9034 | -0.6073%
Barometric pressure true as of 558AM Jan 7 was 1007.6 mb -- but last column very insensitive to pressure within a 100mb range
Points for graph for 645AM Jan 7
|  | T In C | RH in | Tout C | RH out
|  | 18.1444 | 34.03 | 43.1111 | 9.17
|  | W: | 0.004401 | W: | 0.0049609
|  | abs hum*10 | air-s enthalph | abs hum | air-s enthalph
| In | 0.0043817 | 29.4018
| Out | 0.0049364 | 56.1823
|  |  | xw | hl
|  |  | g/kg air | kJ/kg(dryair)
|  |  | 4.401 | 29.5312
|  |  | 4.9609 | 56.461

## density
Density of Moist Air from cp_ptW_HAP_IP
Assumed Pressure |  | 14.6959 | PSI (Standard atmosphere)
| Relative Humidity | [27 empty] | Specific volume dry
Temperature F | 0% | 20% | 22% | 24% | 26% | 28% | 30% | 32% | 34% | 36% | 38% | 40% | 42% | 44% | 46% | 48% | 50% | 52% | 54% | 56% | 58% | 60% | 62% | 64% | 66% | 68% | 70% | 100% | 1/B_ | From table 2
55 | 0.077106 | 0.077021 | 0.077013 | 0.077004 | 0.076996 | 0.076987 | 0.076979 | 0.076971 | 0.076962 | 0.076954 | 0.076945 | 0.076937 | 0.076928 | 0.07692 | 0.076911 | 0.076903 | 0.076894 | 0.076886 | 0.076877 | 0.076869 | 0.07686 | 0.076852 | 0.076844 | 0.076835 | 0.076827 | 0.076818 | 0.07681 | 0.076683 | 12.9691 | 12.969
56 | 0.076956 | 0.076868 | 0.07686 | 0.076851 | 0.076842 | 0.076833 | 0.076825 | 0.076816 | 0.076807 | 0.076798 | 0.076789 | 0.076781 | 0.076772 | 0.076763 | 0.076754 | 0.076746 | 0.076737 | 0.076728 | 0.076719 | 0.076711 | 0.076702 | 0.076693 | 0.076684 | 0.076676 | 0.076667 | 0.076658 | 0.076649 | 0.076518 | 12.9944 | 12.994
57 | 0.076807 | 0.076716 | 0.076707 | 0.076698 | 0.076689 | 0.07668 | 0.076671 | 0.076661 | 0.076652 | 0.076643 | 0.076634 | 0.076625 | 0.076616 | 0.076607 | 0.076598 | 0.076589 | 0.07658 | 0.076571 | 0.076562 | 0.076553 | 0.076544 | 0.076535 | 0.076526 | 0.076516 | 0.076507 | 0.076498 | 0.076489 | 0.076354 | 13.0197 | 13.02
58 | 0.076658 | 0.076564 | 0.076555 | 0.076545 | 0.076536 | 0.076526 | 0.076517 | 0.076508 | 0.076498 | 0.076489 | 0.076479 | 0.07647 | 0.076461 | 0.076451 | 0.076442 | 0.076433 | 0.076423 | 0.076414 | 0.076404 | 0.076395 | 0.076386 | 0.076376 | 0.076367 | 0.076358 | 0.076348 | 0.076339 | 0.076329 | 0.076189 | 13.045 | 13.045
59 | 0.07651 | 0.076412 | 0.076403 | 0.076393 | 0.076383 | 0.076374 | 0.076364 | 0.076354 | 0.076344 | 0.076335 | 0.076325 | 0.076315 | 0.076306 | 0.076296 | 0.076286 | 0.076277 | 0.076267 | 0.076257 | 0.076247 | 0.076238 | 0.076228 | 0.076218 | 0.076209 | 0.076199 | 0.076189 | 0.07618 | 0.07617 | 0.076025 | 13.0702 | 13.07
60 | 0.076362 | 0.076261 | 0.076251 | 0.076241 | 0.076231 | 0.076221 | 0.076211 | 0.076201 | 0.076191 | 0.076181 | 0.076171 | 0.076161 | 0.076151 | 0.076141 | 0.076131 | 0.076121 | 0.076111 | 0.076101 | 0.076091 | 0.076081 | 0.076071 | 0.076061 | 0.076051 | 0.076041 | 0.076031 | 0.076021 | 0.076011 | 0.07586 | 13.0955 | 13.096
61 | 0.076215 | 0.076111 | 0.076101 | 0.07609 | 0.07608 | 0.076069 | 0.076059 | 0.076049 | 0.076038 | 0.076028 | 0.076017 | 0.076007 | 0.075997 | 0.075986 | 0.075976 | 0.075966 | 0.075955 | 0.075945 | 0.075934 | 0.075924 | 0.075914 | 0.075903 | 0.075893 | 0.075883 | 0.075872 | 0.075862 | 0.075851 | 0.075696 | 13.1208 | 13.121
62 | 0.076068 | 0.075961 | 0.07595 | 0.075939 | 0.075929 | 0.075918 | 0.075907 | 0.075896 | 0.075886 | 0.075875 | 0.075864 | 0.075853 | 0.075843 | 0.075832 | 0.075821 | 0.075811 | 0.0758 | 0.075789 | 0.075778 | 0.075768 | 0.075757 | 0.075746 | 0.075735 | 0.075725 | 0.075714 | 0.075703 | 0.075693 | 0.075532
63 | 0.075922 | 0.075811 | 0.0758 | 0.075789 | 0.075778 | 0.075767 | 0.075756 | 0.075745 | 0.075733 | 0.075722 | 0.075711 | 0.0757 | 0.075689 | 0.075678 | 0.075667 | 0.075656 | 0.075645 | 0.075634 | 0.075623 | 0.075611 | 0.0756 | 0.075589 | 0.075578 | 0.075567 | 0.075556 | 0.075545 | 0.075534 | 0.075368
64 | 0.075777 | 0.075662 | 0.075651 | 0.075639 | 0.075628 | 0.075616 | 0.075605 | 0.075593 | 0.075582 | 0.07557 | 0.075559 | 0.075547 | 0.075536 | 0.075524 | 0.075513 | 0.075501 | 0.07549 | 0.075478 | 0.075467 | 0.075456 | 0.075444 | 0.075433 | 0.075421 | 0.07541 | 0.075398 | 0.075387 | 0.075375 | 0.075204
65 | 0.075632 | 0.075513 | 0.075502 | 0.07549 | 0.075478 | 0.075466 | 0.075454 | 0.075442 | 0.07543 | 0.075418 | 0.075407 | 0.075395 | 0.075383 | 0.075371 | 0.075359 | 0.075347 | 0.075335 | 0.075324 | 0.075312 | 0.0753 | 0.075288 | 0.075276 | 0.075264 | 0.075253 | 0.075241 | 0.075229 | 0.075217 | 0.07504
66 | 0.075488 | 0.075365 | 0.075353 | 0.075341 | 0.075328 | 0.075316 | 0.075304 | 0.075292 | 0.075279 | 0.075267 | 0.075255 | 0.075242 | 0.07523 | 0.075218 | 0.075206 | 0.075193 | 0.075181 | 0.075169 | 0.075157 | 0.075144 | 0.075132 | 0.07512 | 0.075108 | 0.075096 | 0.075083 | 0.075071 | 0.075059 | 0.074876
67 | 0.075344 | 0.075217 | 0.075205 | 0.075192 | 0.075179 | 0.075167 | 0.075154 | 0.075141 | 0.075129 | 0.075116 | 0.075103 | 0.075091 | 0.075078 | 0.075065 | 0.075053 | 0.07504 | 0.075027 | 0.075015 | 0.075002 | 0.074989 | 0.074977 | 0.074964 | 0.074951 | 0.074939 | 0.074926 | 0.074913 | 0.074901 | 0.074711
68 | 0.075201 | 0.07507 | 0.075057 | 0.075044 | 0.075031 | 0.075017 | 0.075004 | 0.074991 | 0.074978 | 0.074965 | 0.074952 | 0.074939 | 0.074926 | 0.074913 | 0.0749 | 0.074887 | 0.074874 | 0.074861 | 0.074847 | 0.074834 | 0.074821 | 0.074808 | 0.074795 | 0.074782 | 0.074769 | 0.074756 | 0.074743 | 0.074547
69 | 0.075058 | 0.074923 | 0.074909 | 0.074896 | 0.074882 | 0.074869 | 0.074855 | 0.074842 | 0.074828 | 0.074815 | 0.074801 | 0.074788 | 0.074774 | 0.074761 | 0.074747 | 0.074734 | 0.07472 | 0.074707 | 0.074693 | 0.07468 | 0.074666 | 0.074653 | 0.074639 | 0.074626 | 0.074612 | 0.074599 | 0.074585 | 0.074383
70 | 0.074916 | 0.074776 | 0.074762 | 0.074748 | 0.074734 | 0.07472 | 0.074706 | 0.074693 | 0.074679 | 0.074665 | 0.074651 | 0.074637 | 0.074623 | 0.074609 | 0.074595 | 0.074581 | 0.074567 | 0.074553 | 0.074539 | 0.074525 | 0.074511 | 0.074497 | 0.074483 | 0.074469 | 0.074455 | 0.074442 | 0.074428 | 0.074219
71 | 0.074775 | 0.07463 | 0.074616 | 0.074601 | 0.074587 | 0.074572 | 0.074558 | 0.074544 | 0.074529 | 0.074515 | 0.0745 | 0.074486 | 0.074472 | 0.074457 | 0.074443 | 0.074428 | 0.074414 | 0.0744 | 0.074385 | 0.074371 | 0.074356 | 0.074342 | 0.074328 | 0.074313 | 0.074299 | 0.074284 | 0.07427 | 0.074055
72 | 0.074634 | 0.074484 | 0.07447 | 0.074455 | 0.07444 | 0.074425 | 0.07441 | 0.074395 | 0.07438 | 0.074365 | 0.07435 | 0.074336 | 0.074321 | 0.074306 | 0.074291 | 0.074276 | 0.074261 | 0.074246 | 0.074231 | 0.074217 | 0.074202 | 0.074187 | 0.074172 | 0.074157 | 0.074142 | 0.074127 | 0.074113 | 0.07389
73 | 0.074493 | 0.074339 | 0.074324 | 0.074308 | 0.074293 | 0.074278 | 0.074262 | 0.074247 | 0.074232 | 0.074216 | 0.074201 | 0.074185 | 0.07417 | 0.074155 | 0.074139 | 0.074124 | 0.074109 | 0.074093 | 0.074078 | 0.074063 | 0.074047 | 0.074032 | 0.074017 | 0.074001 | 0.073986 | 0.073971 | 0.073955 | 0.073726
74 | 0.074353 | 0.074194 | 0.074178 | 0.074162 | 0.074147 | 0.074131 | 0.074115 | 0.074099 | 0.074083 | 0.074067 | 0.074051 | 0.074036 | 0.07402 | 0.074004 | 0.073988 | 0.073972 | 0.073956 | 0.07394 | 0.073925 | 0.073909 | 0.073893 | 0.073877 | 0.073861 | 0.073845 | 0.07383 | 0.073814 | 0.073798 | 0.073561
75 | 0.074214 | 0.07405 | 0.074033 | 0.074017 | 0.074 | 0.073984 | 0.073968 | 0.073951 | 0.073935 | 0.073919 | 0.073902 | 0.073886 | 0.07387 | 0.073853 | 0.073837 | 0.07382 | 0.073804 | 0.073788 | 0.073771 | 0.073755 | 0.073739 | 0.073722 | 0.073706 | 0.07369 | 0.073673 | 0.073657 | 0.073641 | 0.073396
Dry air component of density only
| Relative Humidity | [27 empty] | Specific Volume sat
Temperature F | 0% | 20% | 22% | 24% | 26% | 28% | 30% | 32% | 34% | 36% | 38% | 40% | 42% | 44% | 46% | 48% | 50% | 52% | 54% | 56% | 58% | 60% | 62% | 64% | 66% | 68% | 70% | 100% | 1/AC_ | From Table 2
55 | 0.077106 | 0.076881 | 0.076859 | 0.076836 | 0.076814 | 0.076791 | 0.076768 | 0.076746 | 0.076723 | 0.076701 | 0.076678 | 0.076656 | 0.076633 | 0.076611 | 0.076588 | 0.076566 | 0.076543 | 0.076521 | 0.076498 | 0.076476 | 0.076454 | 0.076431 | 0.076409 | 0.076386 | 0.076364 | 0.076341 | 0.076319 | 0.075981 | 13.1611 | 13.161
56 | 0.076956 | 0.076723 | 0.0767 | 0.076677 | 0.076653 | 0.07663 | 0.076607 | 0.076583 | 0.07656 | 0.076537 | 0.076514 | 0.07649 | 0.076467 | 0.076444 | 0.07642 | 0.076397 | 0.076374 | 0.076351 | 0.076327 | 0.076304 | 0.076281 | 0.076257 | 0.076234 | 0.076211 | 0.076188 | 0.076164 | 0.076141 | 0.075792 | 13.194 | 13.194
57 | 0.076807 | 0.076566 | 0.076542 | 0.076517 | 0.076493 | 0.076469 | 0.076445 | 0.076421 | 0.076397 | 0.076373 | 0.076349 | 0.076325 | 0.076301 | 0.076276 | 0.076252 | 0.076228 | 0.076204 | 0.07618 | 0.076156 | 0.076132 | 0.076108 | 0.076084 | 0.07606 | 0.076035 | 0.076011 | 0.075987 | 0.075963 | 0.075602 | 13.2272 | 13.227
58 | 0.076658 | 0.076408 | 0.076384 | 0.076359 | 0.076334 | 0.076309 | 0.076284 | 0.076259 | 0.076234 | 0.076209 | 0.076184 | 0.076159 | 0.076134 | 0.076109 | 0.076084 | 0.076059 | 0.076034 | 0.076009 | 0.075985 | 0.07596 | 0.075935 | 0.07591 | 0.075885 | 0.07586 | 0.075835 | 0.07581 | 0.075785 | 0.075411 | 13.2606 | 13.261
59 | 0.07651 | 0.076252 | 0.076226 | 0.0762 | 0.076174 | 0.076148 | 0.076123 | 0.076097 | 0.076071 | 0.076045 | 0.076019 | 0.075994 | 0.075968 | 0.075942 | 0.075916 | 0.07589 | 0.075865 | 0.075839 | 0.075813 | 0.075787 | 0.075762 | 0.075736 | 0.07571 | 0.075684 | 0.075658 | 0.075633 | 0.075607 | 0.07522 | 13.2943 | 13.294
60 | 0.076362 | 0.076095 | 0.076068 | 0.076042 | 0.076015 | 0.075988 | 0.075962 | 0.075935 | 0.075908 | 0.075882 | 0.075855 | 0.075828 | 0.075802 | 0.075775 | 0.075748 | 0.075722 | 0.075695 | 0.075668 | 0.075641 | 0.075615 | 0.075588 | 0.075561 | 0.075535 | 0.075508 | 0.075481 | 0.075455 | 0.075428 | 0.075028 | 13.3283 | 13.328
61 | 0.076215 | 0.075939 | 0.075911 | 0.075884 | 0.075856 | 0.075828 | 0.075801 | 0.075773 | 0.075746 | 0.075718 | 0.07569 | 0.075663 | 0.075635 | 0.075608 | 0.07558 | 0.075553 | 0.075525 | 0.075497 | 0.07547 | 0.075442 | 0.075415 | 0.075387 | 0.075359 | 0.075332 | 0.075304 | 0.075277 | 0.075249 | 0.074836 | 13.3626 | 13.363
62 | 0.076068 | 0.075783 | 0.075754 | 0.075726 | 0.075697 | 0.075669 | 0.07564 | 0.075612 | 0.075583 | 0.075555 | 0.075526 | 0.075498 | 0.075469 | 0.07544 | 0.075412 | 0.075383 | 0.075355 | 0.075326 | 0.075298 | 0.075269 | 0.075241 | 0.075212 | 0.075184 | 0.075155 | 0.075127 | 0.075098 | 0.07507 | 0.074642
63 | 0.075922 | 0.075627 | 0.075598 | 0.075568 | 0.075539 | 0.075509 | 0.07548 | 0.07545 | 0.075421 | 0.075391 | 0.075362 | 0.075332 | 0.075303 | 0.075273 | 0.075244 | 0.075214 | 0.075185 | 0.075155 | 0.075126 | 0.075096 | 0.075067 | 0.075037 | 0.075008 | 0.074978 | 0.074949 | 0.074919 | 0.07489 | 0.074448
64 | 0.075777 | 0.075472 | 0.075441 | 0.075411 | 0.07538 | 0.07535 | 0.075319 | 0.075289 | 0.075258 | 0.075228 | 0.075197 | 0.075167 | 0.075136 | 0.075106 | 0.075075 | 0.075045 | 0.075014 | 0.074984 | 0.074953 | 0.074923 | 0.074893 | 0.074862 | 0.074832 | 0.074801 | 0.074771 | 0.07474 | 0.07471 | 0.074253
65 | 0.075632 | 0.075317 | 0.075285 | 0.075254 | 0.075222 | 0.075191 | 0.075159 | 0.075128 | 0.075096 | 0.075065 | 0.075033 | 0.075002 | 0.07497 | 0.074939 | 0.074907 | 0.074876 | 0.074844 | 0.074812 | 0.074781 | 0.074749 | 0.074718 | 0.074686 | 0.074655 | 0.074623 | 0.074592 | 0.07456 | 0.074529 | 0.074057
66 | 0.075488 | 0.075162 | 0.075129 | 0.075097 | 0.075064 | 0.075032 | 0.074999 | 0.074966 | 0.074934 | 0.074901 | 0.074869 | 0.074836 | 0.074804 | 0.074771 | 0.074738 | 0.074706 | 0.074673 | 0.074641 | 0.074608 | 0.074576 | 0.074543 | 0.074511 | 0.074478 | 0.074445 | 0.074413 | 0.07438 | 0.074348 | 0.07386
67 | 0.075344 | 0.075007 | 0.074974 | 0.07494 | 0.074906 | 0.074873 | 0.074839 | 0.074805 | 0.074772 | 0.074738 | 0.074704 | 0.074671 | 0.074637 | 0.074603 | 0.07457 | 0.074536 | 0.074503 | 0.074469 | 0.074435 | 0.074402 | 0.074368 | 0.074334 | 0.074301 | 0.074267 | 0.074233 | 0.0742 | 0.074166 | 0.073662
68 | 0.075201 | 0.074853 | 0.074818 | 0.074783 | 0.074749 | 0.074714 | 0.074679 | 0.074644 | 0.07461 | 0.074575 | 0.07454 | 0.074505 | 0.07447 | 0.074436 | 0.074401 | 0.074366 | 0.074331 | 0.074297 | 0.074262 | 0.074227 | 0.074192 | 0.074158 | 0.074123 | 0.074088 | 0.074053 | 0.074019 | 0.073984 | 0.073463
69 | 0.075058 | 0.074699 | 0.074663 | 0.074627 | 0.074591 | 0.074555 | 0.074519 | 0.074483 | 0.074447 | 0.074411 | 0.074376 | 0.07434 | 0.074304 | 0.074268 | 0.074232 | 0.074196 | 0.07416 | 0.074124 | 0.074088 | 0.074052 | 0.074017 | 0.073981 | 0.073945 | 0.073909 | 0.073873 | 0.073837 | 0.073801 | 0.073263
70 | 0.074916 | 0.074545 | 0.074508 | 0.074471 | 0.074434 | 0.074397 | 0.074359 | 0.074322 | 0.074285 | 0.074248 | 0.074211 | 0.074174 | 0.074137 | 0.0741 | 0.074063 | 0.074026 | 0.073989 | 0.073951 | 0.073914 | 0.073877 | 0.07384 | 0.073803 | 0.073766 | 0.073729 | 0.073692 | 0.073655 | 0.073618 | 0.073062
71 | 0.074775 | 0.074391 | 0.074353 | 0.074315 | 0.074276 | 0.074238 | 0.0742 | 0.074161 | 0.074123 | 0.074085 | 0.074046 | 0.074008 | 0.07397 | 0.073932 | 0.073893 | 0.073855 | 0.073817 | 0.073778 | 0.07374 | 0.073702 | 0.073663 | 0.073625 | 0.073587 | 0.073549 | 0.07351 | 0.073472 | 0.073434 | 0.07286
72 | 0.074634 | 0.074238 | 0.074198 | 0.074159 | 0.074119 | 0.074079 | 0.07404 | 0.074 | 0.073961 | 0.073921 | 0.073882 | 0.073842 | 0.073803 | 0.073763 | 0.073724 | 0.073684 | 0.073644 | 0.073605 | 0.073565 | 0.073526 | 0.073486 | 0.073447 | 0.073407 | 0.073368 | 0.073328 | 0.073289 | 0.073249 | 0.072657
73 | 0.074493 | 0.074084 | 0.074044 | 0.074003 | 0.073962 | 0.073921 | 0.07388 | 0.073839 | 0.073799 | 0.073758 | 0.073717 | 0.073676 | 0.073635 | 0.073594 | 0.073554 | 0.073513 | 0.073472 | 0.073431 | 0.07339 | 0.073349 | 0.073309 | 0.073268 | 0.073227 | 0.073186 | 0.073145 | 0.073105 | 0.073064 | 0.072452
74 | 0.074353 | 0.073931 | 0.073889 | 0.073847 | 0.073805 | 0.073763 | 0.07372 | 0.073678 | 0.073636 | 0.073594 | 0.073552 | 0.07351 | 0.073468 | 0.073425 | 0.073383 | 0.073341 | 0.073299 | 0.073257 | 0.073215 | 0.073173 | 0.07313 | 0.073088 | 0.073046 | 0.073004 | 0.072962 | 0.07292 | 0.072878 | 0.072246
75 | 0.074214 | 0.073778 | 0.073735 | 0.073691 | 0.073648 | 0.073604 | 0.073561 | 0.073517 | 0.073474 | 0.07343 | 0.073387 | 0.073343 | 0.0733 | 0.073256 | 0.073213 | 0.073169 | 0.073126 | 0.073082 | 0.073039 | 0.072995 | 0.072952 | 0.072908 | 0.072865 | 0.072821 | 0.072778 | 0.072734 | 0.072691 | 0.072039