## 118 Raw Balometer Notes (hidden)
All vents blocked except basement
Flow measured is 269, 309, 314,300,313
Power draw is 78-79 steady
Set fan to low
drops to 51 52
Speed is 248, 238, 2xx | 300 | 78
| 248 | 51
| 1.2097 | 1.5294 | 1.7701
Now, open bathroom vent | [10 empty] | Fan Load from History
Showing backpressure corrected numbers | [7 empty] | Measurement time |  |  | Avg in Per | 2x Avg *1000
Basement | 300 | 314 | 300 | 313 |  | Fan high alone | 78-79 | 6:35AM | Weds, 12/13 |  | 0.039175 | 78.35
Basement | 248 | 238 | 214 |  |  | Fan low | 51 | 6:39AM, 6:42 |  |  | 0.0257 | 51.4
Basement | 196 |  |  |  |  | Fan low | 54 | 6:46 | 6:48
Basement | 300 | 266 | 297 |  |  | Fan high | 82 | 6:51 | 6:51 | 6:52 | 0.0406 | 81.2
Bathroom | 185 | 186 |  |  |  | Fan high | 82 | 6:56 | 6:56
Basemen | 209 | 217 |  |  |  | Fan high | 90 | 7:04 | 7:04 |  | 0.04408 | 88.16
Bathroom | 177 | 171 |  |  |  | Fan high | 88 | 7:00 | 7:00
Stdy | 199 | 218 | 215 |  |  | Fan high | 90 | 7:02 | 7:02 | 7:02
Basementr | 205 | 198 |  |  |  | Fan high | 91 | 7:09 | 7:09 |  | 0.04549 | 90.98
Bathroom | 160 | 164 |  |  |  | Fan high | 91 | 7:13 | 7:13
Study | 200 | 214 |  |  |  | Fan high | 90 | 7:15 | 7:15
Kitchen | 135 | 127 |  |  |  | Fan high | 92 | 7:11 | 7:11
Basementr | 187 | 190 |  |  |  | Fan high | 94 | 7:26 | 7:26 |  | 0.04667 | 93.34
Bathroom | 137 | 145 |  |  |  | Fan high | 92 | 7:24 | 7:24
Study | 180 | 178 |  |  |  | Fan high | 93 | 7:22 | 7:22
Kitchen | 101 | 104 |  |  |  | Fan high | 94 | 7:19 | 7:19
Dining Room | 132 | 135 |  |  |  | Fan high | 93 | 7:20 | 7:20
Basementr | 162 | 167 |  |  |  | Fan high |  | 7:40 | 7:40 |  | 0.047333 | 94.666
Bathroom | 125 | 121 |  |  |  | Fan high | 96 | 7:38 | 7:38
Study | 169 | 173 |  |  |  | Fan high | 96 | 7:36 | 7:36
Kitchen | 111 | 113 |  |  |  | Fan high | 94 | 7:31 | 7:31
Dining Room | 103 | 117 |  |  |  | Fan high | 96 | 7:33 | 7:33
Living Room | 108 | 106 |  |  |  | Fan high | 96 | 7:34 | 7:34
Basement | 160 | 164 | 179 |  |  | Fan high | 96 | 7:44 | 7:44 | 7:44 | 0.047546 | 95.0917 | .04775 in 9:39 error reread
Bathroom | 71 | 91 | 82 |  |  | Fan high | 95 | 7:46 | 7:46 | 7:46
Study | 154 | 154 |  |  |  | Fan high |  | 7:47 | 7:47
Kitchen | 101 | 101 |  |  |  | Fan high |  | 7:48 | 7:48
Dining Room | 70 | 85 | 87 |  |  | Fan high |  | 7:50 | 7:50 | 7:50
Living Room | 77 | 84 | 78 | 73 |  | Fan high | 96 | 7:51 | 7:51
Gym | 112 | 117 | 106 | 119 | 112 | Fan high |  | 7:55 | 7:55 | 9:39 | 9:39 | 9:39
Hall | 84 | 99 | 101 | 85 | 88 | Fan high |  | 7:55 | 7:55 | 7:55 | 9:43 | 9:43
Basement | 160 | 163 |  |  |  | Fan high |  | 10:00 | 10:00 |  | 0.047417 | 94.8333 |  |  | From Greg
Bathroom | 81 | 71 |  |  |  | Fan high |  | 9:55 | 9:55 |  |  |  |  | Bath | 74
Study | 176 | 175 |  |  |  | Fan high |  | 9:56 | 9:56 |  |  |  |  | Study | 157
Kitchen | 99 | 101 |  |  |  | Fan high |  | 9:57 | 9:58 |  |  |  |  | Kitchen | 117
Dining Room | 70 | 80 |  |  |  | Fan high |  | 9:46 | 9:46 |  |  |  |  | Dining | 71
Living Room | 77 | 73 |  |  |  | Fan high |  | 9:50 | 9:50
Gym | 98 | 105 |  |  |  | Fan high | 94-98 | 9:48 | 9:48 |  |  |  |  | Gym | 111
Hall | 86 | 86 |  |  |  | Fan high |  | 9:51 | 9:51 |  |  |  |  | Entry | 82
Bedroom | 68 | 72 | [5 empty] | 9:55 | 9:55 |  |  |  |  | Bedroom | 53
| 915 | 926 | [10 empty] | 665 |  | 665
| 678 | 690
Fan high

## 118 Compiled balometer
Balometer Readings with BackPressure Correction (Grey cells indicate duct blocked during measurement) | [9 empty] | Without Correction
| Measurement start times on Wednesday, December 13 | [8 empty] | 2023-12-15
HC Supply Vents | 06:35AM | 06:39AM | 06:51AM | 07:00AM | 07:09AM | 07:19AM | 07:31AM | 07:44AM | 09:46AM | 10:02AM through 10:30AM
Basement | 306.75 | 233.3333 | 287.6667 | 213 | 201.5 | 188.5 | 164.5 | 162 | 161.5 | 127 | 127 | 137
Bathroom |  |  | 185.5 | 174 | 162 | 141 | 123 | 81 | 76 | 58 | 52 | 56
Study |  |  |  | 210.6667 | 207 | 179 | 171 | 154 | 175.5 | 148 | 146 | 146
Kitchen |  |  |  |  | 131 | 102.5 | 112 | 101 | 100 | 82 | 82 | 84
Dining Room | [5 empty] | 133.5 | 110 | 77.5 | 75 | 56 | 57 | 55
Living Room | [6 empty] | 107 | 80.5 | 75 | 72 | 68 | 72
Gym | [7 empty] | 113.2 | 101.5 | 80 | 79 | 80
Hall | [7 empty] | 91.4 | 86 | 72 | 70 | 72
Bedroom | [8 empty] | 70 | 37 | 44 | 40
Total CFM | 306.75 | 233.3333 | 473.1667 | 597.6667 | 701.5 | 744.5 | 787.5 | 860.6 | 920.5 | 732 | 725 | 742 | 733 | 2.3863 | 0.41906 | 0.76066
Average KW from history* | 78.35 | 51.4 | 81.2 | 88.16 | 90.98 | 93.34 | 94.666 | 95.09 | 94.83 | 94.2985 | average* |  |  |  | 0.83087 | 0.65603 | 0.28234
Fan Setting | "High"/HH | "Low"/L | "High"/HH | "High"/HH | "High"/HH | "High"/HH | "High"/HH | "High"/HH | "High"/HH | "High"/HH | "High"/HH | "High"/HH
*Checks to instantaneous observations by minute on 12/13
** Based on by second average on 12/15 -- max single lead second 50.6w; min single lead second 44.1w; average includes 1800x2 observations
[12 empty] | 40 | 0.52857
[12 empty] | 55 | 0.74667
[12 empty] | 56 | 0.76316
[12 empty] | 72 | 0.96
[12 empty] | 72 | 0.83721
[12 empty] | 80 | 0.78818
[12 empty] | 84 | 0.82
[12 empty] | 137 | 0.78638
[12 empty] | 146 | 0.8433

## 118 Remeasure for comparisons
Lessons from experiment with four vents, columns F through AD hidden
(1) Hood smooths flow. Local turbulence can confuse the Alnor EBT731's monitoring grid -- measurement without the hood leads to varying results -- found in columns F through S, hidden
(1A) Probably no difference between hoods, but not carefully studied -- columns T through AD
(2) Probably, it should be a field practice to not use backpressure correction if one gets the open>closed error
(3) Remeasure with hood on is fairly close to before | [31 empty] | ` | [5 empty] | ERV DEFINITELY OFF |  |  |  |  | ERV DEFINITELY ON |  |  |  |  | ERV DEFINITELY OFF |  |  |  |  | ERV DEFINITELY ON
[6 empty] | Measurements on 12-19, from 11:45, NO HOOD, RIGHT SIDE UP (ERV OFF 90% OF TIME -= WAS ON 10% SETTING ) | [6 empty] | SAME UPSIDE DOWN | [6 empty] | REMEASURE, WITH SQUARE HOOD RIGHT SIDE UP | [7 empty] | REMEASURE, WITH SQUARE HOOD, using straight mode |  |  |  | REMEASURE ALL WITH RECTANGULAR HOOD | [5 empty] | REMEASURE ALL WITH RECTANGULAR HOOD, 12/30 AT 4:45 TO 5:10 |  |  |  |  | REMEASURE ALL WITH RECTANGULAR HOOD, 12/30 AT 5:10 TO 5:30 |  |  |  |  | REMEASURE ALL WITH RECTANGULAR HOOD, 12/30 AT 5:40 TO 5:50 (PAUSED FOR SYSTEM DOWN) AND 6:02 TO 6:10 |  |  |  |  | REMEASURE ALL WITH RECTANGULAR HOOD, 12/30 AT 6:14 TO
| Prior no correction measurements, 12-15 |  |  |  |  | Initial | Corrected | Initial | Corrected | Initial | Corrected | Avg Init | Initial | Corrected | Initial | Corrected | Initial | Corrected | Avg Init | Initial | Corrected | Initial | Corrected | Initial | Corrected | Avg Init | Avg Cor | Open | Open | Open | Avg Init | Open | Open | Open |  |  |  | Open | Open | Open |  |  | Open | Open | Open |  |  | Open | Open | Open |  |  | Open | Open | Open | [5 empty] | Consider groups and discard min and max group, so average four #'s
Comparison base -- all vents open | 1st | 2d | 3rd | AVG | Avg as % of total sample average | [26 empty] | 1st | 2d | 3rd | AVG | Avg as % of total sample average | 1st | 2d | 3rd | AVG | Avg as % of total sample average | 1st | 2d | 3rd | AVG | Avg as % of total sample average | 1st | 2d | 3rd | AVG | Avg as % of total sample average | 1st | 2d | 3rd | AVG | Avg as % of total sample average | Var.p | stdev.p | mean | stdev.p/mean | Avg six groups | min | max | Avg 4 middle groups
Basement | 127 | 127 | 137 | 130.3333 | 6.685% | [26 empty] | 106 | 118 | 114 | 112.6667 | -7.776% | 119 | 124 | 122 | 121.6667 | -0.4093% | 119 | 109 | 112 | 113.3333 | -7.231% | 140 | 136 | 135 | 137 | 12.14% | 115 | 118 | 121 | 118 | -3.411% | 92.0278 | 9.5931 | 122.1667 | 7.852% | 122.1667 | 112.6667 | 137 | 120.8333
Bathroom | 58 | 52 | 56 | 55.3333 | -0.6979% | [26 empty] | 58 | 55 | 55 | 56 | 0.4985% | 51 | 49 | 51 | 50.3333 | -9.671% | 52 | 51 | 50 | 51 | -8.475% | 64 | 57 | 62 | 61 | 9.472% | 63 | 60 | 59 | 60.6667 | 8.873% | 20.8673 | 4.5681 | 55.7222 | 8.198% | 55.7222 | 50.3333 | 61 | 55.75
Study | 148 | 146 | 146 | 146.6667 | 10.97% | [26 empty] | 129 | 129 | 129 | 129 | -2.396% | 128 | 127 | 132 | 129 | -2.396% | 129 | 130 | 130 | 129.6667 | -1.892% | 130 | 129 | 128 | 129 | -2.396% | 129 | 130 | 130 | 129.6667 | -1.892% | 43.25 | 6.5765 | 132.1667 | 4.976% | 132.1667 | 129 | 146.6667 | 129.3333
Kitchen | 82 | 82 | 84 | 82.6667 | -15.74% | 162 | ERR | 158 | 208 | 162 | ERR | 160.6667 | -130 | ERR | -131 | ERR | -131 | ERR | -130.6667 | 87 | 114 | 88 | 115 | 85 | 111 | 86.6667 | 113.3333 | 80 | 79 | 83 | 80.6667 | 90 | 88 | 90 | 89.3333 | -8.947% | 116 | 117 | 112 | 115 | 17.21% | 100 | 92 | 96 | 96 | -2.152% | 115 | 118 | 119 | 117.3333 | 19.59% | 84 | 91 | 90 | 88.3333 | -9.966% | 183.321 | 13.5396 | 98.1111 | 13.8% | 98.1111 | 82.6667 | 117.3333 | 97.1667
Dining Room | 56 | 57 | 55 | 56 | -9.677% | 79 | ERR | 80 | 106 | 82 | 108 | 80.3333 | -74 | ERR | -86 | ERR | -75 | ERR | -78.3333 | 61 | 72 | 58 | 67 | 59 | 69 | 59.3333 | 69.3333 | 61 | 60 | 61 | 60.6667 | 66 | 67 | 63 | 65.3333 | 5.376% | 66 | 70 | 69 | 68.3333 | 10.22% | 58 | 58 | 58 | 58 | -6.452% | 64 | 60 | 65 | 63 | 1.613% | 63 | 62 | 59 | 61.3333 | -1.075% | 19.7778 | 4.4472 | 62 | 7.173% | 62 | 56 | 68.3333 | 61.9167
Living Room | 72 | 68 | 72 | 70.6667 | -3.927% | 95 | 124 | 99 | ERR | 99 | ERR | 97.6667 | -105 | -119 | -108 | ERR | -103 | ERR | -105.3333 | 70 | 91 | 65 | 75 | 66 | 81 | 67 | 82.3333 | 70 | 68 | 69 | 69 | 65 | 69 | 68 | 67.3333 | -8.459% | 81 | 78 | 76 | 78.3333 | 6.495% | 69 | 67 | 69 | 68.3333 | -7.1% | 82 | 83 | 78 | 81 | 10.12% | 76 | 75 | 76 | 75.6667 | 2.87% | 28.9136 | 5.3771 | 73.5556 | 7.31% | 73.5556 | 67.3333 | 81 | 73.25
Gym | 80 | 79 | 80 | 79.6667 | 24.37% | [26 empty] | 69 | 68 | 71 | 69.3333 | 8.239% | 69 | 61 | 60 | 63.3333 | -1.127% | 62 | 61 | 63 | 62 | -3.209% | 55 | 62 | 58 | 58.3333 | -8.933% | 53 | 52 | 50 | 51.6667 | -19.34% | 81.8302 | 9.046 | 64.0556 | 14.12% | 64.0556 | 51.6667 | 79.6667 | 63.25
Hall | 72 | 70 | 72 | 71.3333 | -3.459% | [26 empty] | 71 | 71 | 72 | 71.3333 | -3.459% | 76 | 72 | 75 | 74.3333 | 0.6015% | 73 | 72 | 77 | 74 | 0.1504% | 76 | 78 | 75 | 76.3333 | 3.308% | 76 | 76 | 76 | 76 | 2.857% | 5.6543 | 2.3779 | 73.8889 | 3.218% | 73.8889 | 71.3333 | 76.3333 | 73.9167
Bedroom | 37 | 44 | 40 | 40.3333 | -6.564% | 65 | ERR | 68 | ERR | 68 | ERR |  | -61 | ERR | -63 | ERR | -61 | 67 | [13 empty] | 45 | 45 | 44 | 44.6667 | 3.475% | 42 | 43 | 42 | 42.3333 | -1.931% | 42 | 42 | 41 | 41.6667 | -3.475% | 49 | 46 | 43 | 46 | 6.564% | 43 | 46 | 43 | 44 | 1.931% | 6.4722 | 2.5441 | 43.1667 | 5.894% | 43.1667 | 40.3333 | 46 | 43.1667
Total CFM | 732 | 725 | 742 | 733 | 1.127% | [26 empty] | 699 | 710 | 706 | 705 | -2.736% | 748 | 741 | 739 | 742.6667 | 2.46% | 704 | 682 | 696 | 694 | -4.254% | 775 | 769 | 763 | 769 | 6.093% | 702 | 710 | 704 | 705.3333 | -2.69% | 710.3611 | 26.6526 | 724.8333 | 3.677% | 724.8333 | 661.3333 | 813.3333 | 718.5833
MINUTE BY MINUTE POWER DRAW VERY CLOSE TO CONSTANT AT 91.2 WATTS FOR AIR HANDLER FROM 4:45 TO 5:30 (BOTH MEASUREMENTS)
HOOD CAPTURE OPENING COMPARISON
[35 empty] | Square opening |  | 23 | 23 | 529
[35 empty] | Rect hood |  | 12 | 35 | 420
TESTING STUDY VENT WITH RECTANGULAR HOOD
[32 empty] | ERV ON, DOORS ON BASEMENT ROOM OPEN |  |  | 124 | 124 | 126 | 126 | 123 | 123 | 123 | 123 | 125 | 122 | 123.9
[32 empty] | ERV OFF, DOORS ON BASEMENT ROOM OPEN |  |  | 129 | 126 | 127 | 127 | 125 | 128 | 126 | 127 | 133 | 129 | 127.7
[32 empty] | ERV ON DOORS ON BASEMENT ROOM CLOSED |  |  | 128 | 129 | 127 | 129 | 129 | 127 | 128 | 129 | 129 | 127 | 128.2
[32 empty] | ERV OFF, DOORS ON BASEMENT ROOM CLOSED |  |  | 128 | 127 | 127 | 127 | 130 | 127 | 129 | 129 | 130 | 128 | 128.2
testing bathroom vent with rectangular hood
ERV ON, DOORS ON BASEMENT ROOM OPEN
ERV OFF, DOORS ON BASEMENT ROOM OPEN
[32 empty] | ERV ON DOORS ON BASEMENT ROOM CLOSED |  |  | 54 | 56 | 59 | 60 | 60 | 56 | 61
ERV OFF, DOORS ON BASEMENT ROOM CLOSED

## Anemometer vs Balometer (hidden)
Playing: ANEMOMETER TRAVERSE OF BALOMETER OPENING at top plane
3x3
Over each branch node x 4
Over middle
| Node | Mid/node | Node
Right | 68 | 50 | 53
Center | 46 | 78 | 57
Left | 76 | 91 | 93
Grate is centered more to the left side
HIgher flow on left side, but not ridiculous disparity
Opening approximately 1 ft, read value of 87 not too far off
(Average 68 fpm in values above)

## 118 Anemometer
Area | 36.5 | 9.875 | 360.4375 | 2.503
| 36.625 | 9.75 | 357.0938 | 2.4798 | 0.99072
Fpm | 1 | 2 | 3 | 4 | 5 | 6 | 7
High | 416 | 316 | 351 | 156 | 181 | 212 | 90
Medium | 303 | 168 | 238 | 165 | 290 | 391 | 480
Low | 259 | 185 | 183 | 438 | 479 | 523 | 546
CFM
High | 1041 | 789 | 877 | 389 | 452 | 530 | 224 | 614.5714 | 757.6667 |  | 2023-12-13
Medium | 756 | 420 | 594 | 412 | 724 | 978 | 1199 | 726.1429 |  | High | 1041 | 789 | 877 | 389 | 452 | 530 | 224
Low | 646 | 461 | 456 | 1094 | 1198 | 1307 | 1364 | 932.2857 |  | Med High | 1008 | 532 | 549 | 372 | 419 | 433 | 263
| 0.26389 | 1.9601 | 1.5664 | 1.474 | 1.0499 | 0.6441 | 1.2734 |  |  | Medium | 756 | 420 | 594 | 412 | 724 | 978 | 1199
| 2.4206 | 0.51042 | 1.7231 | 1.0013 | 1.8811 | 0.68793 | 2.4583 |  |  | Med low | 774 | 431 | 543 | 478 | 1449 | 859 | 1174
| 2.2869 | 2.0621 | 2.056 | 2.3307 | 0.9553 | 2.089 | 2.6589 |  |  | Low | 646 | 461 | 456 | 1094 | 1198 | 1307 | 1364
| 814.3333 | 556.6667 | 642.3333 | 631.6667 | 791.3333 | 938.3333 | 929 |  |  |  | 2023-12-11
[10 empty] | upper | 938.6393 | 1026.246 | 916.112 | 543.1593 | 505.6137 | 357.9345 | 340.4132
[10 empty] | middle | 630.7656 | 402.9891 | 645.7839 | 415.5043 | 470.5712 | 1013.73 | 493.0985
|  | middle/low hole 2: 166 | [7 empty] | lower | 728.3841 | 443.0378 | 570.6927 | 503.1107 | 978.6879 | 1239.004 | 958.6636
midle/low/low hoile 4: 676;1690
Fpm | 1 | 2 | 3 | 4 | 5 | 6 | 7
Med High | 403 | 213 | 220 | 149 | 167 | 173 | 105
med low | 310 | 173 | 217 | 191 | 580 | 343 | 469
CFM
Med High | 1008 | 532 | 549 | 372 | 419 | 433 | 263 | 510.8571
Med low | 774 | 431 | 543 | 478 | 1449 | 859 | 1174 | 815.4286
| 0.72439 | 1.1471 | 1.6684 | 0.95269 | -0.99262 | 0.025608 | -0.18099
| 1.9418 | 2.0256 | 0.15929 | 0.080295 | 2.7622 | -0.4579 | -0.075087
NOTE: DURING THIS ENTIRE MEASUREMENT PERIOD (ON WEDNESDAY, DECEMBER 13, FROM 2:30 TO 4:00), Fan power was steady
Average of both leads |  | 0.047024 | 94.0472
Max of either lead |  | 0.0462 | 92.4
Min of either lead |  | 0.0479 | 95.8

## Repeat 118 Traverse, ERV on-off
Log-Tchebycheff Numbers for Rectangle from Alnor Manual
|  |  | 36.625 | 0.053 | 0.203 | 0.366 | 0.5 | 0.634 | 0.797 | 0.947
|  |  | 36.625 | 1.9411 | 7.4349 | 13.4047 | 18.3125 | 23.2203 | 29.1901 | 34.6839
|  | 0.125 |  | 2.0661 | 7.5599 | 13.5297 | 18.4375 | 23.3453 | 29.3151 | 34.8089
| 9.875 |  |  | 1.75 | 5.75 | 11.625 | 17.5 | 23.6 | 29.3 | 34.9
0.926 | 9.1443 | 9.2693
0.712 | 7.031 | 7.156
0.5 | 4.9375 | 5.0625 |  | CROSS SECTION AT MEASUREMENT |  |  |  | 9.75 | 36.625 | 357.0938 | 2.4798
0.288 | 2.844 | 2.969 | [11 empty] | 255 | 633 | 2.4824
0.074 | 0.73075 | 0.85575 | [11 empty] | 322 | 798.8 | 2.4807
798.5013
Positioning of holes: Row is approximately one inch from turn down from above and 4.5 inches back from filter face
At holes, width is 36.875 outside
At holes, height is 10 outside
Meausered inside 9.75 by 36.625
Consider wall width = .125 inch
Note that 0.5 hole is just to left of riser that separates filters
Stove hood turned at some point in the first pass. Off after columns 5-7 in second pass.
Hold times are 20 seconds except 10 seconds in redo of ERV ON Pass
| 11:08, 12:31 | [9 empty] | 2023-12-31 12:11 | [8 empty] | REDO ERV On Pass, Hood off whole time | [8 empty] | REDO ERV OFF Pass, Hood off whole time | [8 empty] | AVERAGE OF 5 35 TRAVERSES, DISCARDING THE HIGH AND LOW BY POINT
| RESULT MATRIX FOR ERV On PASS |  |  |  | 682.5657 | [5 empty] | RESULT MATRIX FOR ERV Off PASS |  |  | 701.42 | [5 empty] | RESULT MATRIX FOR ERV On PASS, 2PM |  |  | 703.7014 | [5 empty] | RESULT MATRIX FOR ERV Off PASS, 1:20PM |  |  | 722.4743 | [5 empty] | 694.0265
| FPM |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | FPM |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | FPM |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | FPM |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | 1 | 445 | 368 | 219 | 129 | 202 | 340 | 160 |  |  | 1 | 496 | 370 | 362 | 188 | 234 | 189 | 105 |  | 1 | 478 | 450 | 425 | 260 | 184 | 338 | 168 |  | 1 | 506 | 415 | 384 | 176 | 185 | 334 | 186
|  | 2 | 394 | 248 | 187 | 142 | 170 | 164 | 127 |  |  | 2 | 403 | 199 | 185 | 166 | 123 | 162 | 134 |  | 2 | 358 | 227 | 310 | 166 | 122 | 123 | 115 |  | 2 | 410 | 185 | 284 | 131 | 173 | 240 | 146
|  | 3 | 258 | 164 | 204 | 142 | 263 | 398 | 361 |  |  | 3 | 332 | 164 | 188 | 159 | 260 | 310 | 292 |  | 3 | 335 | 185 | 235 | 166 | 182 | 341 | 320 |  | 3 | 318 | 188 | 235 | 172 | 276 | 406 | 339
|  | 4 | 270 | 149 | 213 | 212 | 325 | 467 | 455 |  |  | 4 | 328 | 153 | 198 | 206 | 525 | 453 | 453 |  | 4 | 302 | 163 | 199 | 188 | 512 | 437 | 455 |  | 4 | 297 | 161 | 195 | 200 | 333 | 410 | 488
|  | 5 | 244 | 232 | 264 | 379 | 364 | 481 | 496 |  |  | 5 | 419 | 305 | 156 | 188 | 521 | 459 | 519 |  | 5 | 344 | 198 | 132 | 272 | 445 | 356 | 441 |  | 5 | 451 | 231 | 215 | 252 | 393 | 363 | 522
| CFM | 1 | 1102 | 912 | 542.8 | 319.7 | 501.9 | 843.9 | 395.7 |  | CFM | 1 | 1228.6 | 917.6 | 897 | 465.8 | 580.2 | 467.5 | 260.7 | CFM | 1 | 1185.3529 | 1115.918 | 1053.9225 | 644.7526 | 456.2865 | 838.1784 | 416.6094 | CFM | 1 | 1255 | 1029.7 | 951.1 | 436.8 | 459 | 826.9 | 461.5 | 703.1906 | 953.1 | 908.3667 | 430.5333 | 472.3955 | 731.6928 | 357.6698
|  | 2 | 977.8 | 614.3 | 462.8 | 352.3 | 421.6 | 405.9 | 314.6 |  |  | 2 | 998.7 | 493.3 | 457.5 | 412.4 | 305.3 | 400.8 | 332.5 |  | 2 | 887.7747 | 562.9186 | 768.7435 | 411.6497 | 302.5378 | 305.0176 | 285.179 |  | 2 | 1016.7 | 459.3 | 703 | 324.4 | 429.7 | 594.9 | 360.8 | 994.8333 | 529.4062 | 571.6 | 378.6499 | 381.9667 | 413.2333 | 310.7597
|  | 3 | 639.7 | 407.6 | 506.4 | 352.6 | 652.8 | 986.5 | 895 |  |  | 3 | 822.3 | 405.9 | 466 | 393.5 | 643.8 | 768.5 | 724.9 |  | 3 | 830.7389 | 458.7663 | 582.7572 | 411.6497 | 451.3268 | 845.6178 | 793.5417 |  | 3 | 789.6 | 465.6 | 581.5 | 425.3 | 685.3 | 1005.9 | 840.8 | 789.3 | 428.7888 | 556.8857 | 405.7166 | 660.6333 | 936.7059 | 843.1139
|  | 4 | 669.8 | 369.5 | 528.8 | 526.7 | 804.7 | 1158.9 | 1126.9 |  |  | 4 | 813.8 | 378.6 | 491.6 | 512 | 1301.2 | 1123.8 | 1122.4 |  | 4 | 748.9049 | 404.2103 | 493.4837 | 466.2057 | 1269.6667 | 1083.6803 | 1128.3171 |  | 4 | 736.8 | 399.1 | 483.6 | 495.3 | 824.4 | 1016.4 | 1210.6 | 753.235 | 393.9701 | 504.6279 | 495.1 | 1131.7556 | 1074.6268 | 1143.0724
|  | 5 | 604.8 | 574.9 | 653.6 | 938.5 | 901.7 | 1192.9 | 1230.2 |  |  | 5 | 1038.9 | 756.7 | 386.5 | 465.3 | 1291.5 | 1137.1 | 1287.5 |  | 5 | 853.0573 | 491.0039 | 327.3359 | 674.5104 | 1103.5189 | 882.8151 | 1093.5996 |  | 5 | 1118.2 | 573.5 | 534.1 | 625.9 | 973.3 | 899.6 | 1293 | 845.9858 | 546.468 | 458.8667 | 746.3035 | 1091.6063 | 1076.5333 | 1270.2333
| CHECK SUM |  | 1.5189 | 0.57292 | 0.28008 | 0.19648 | -0.97682 | -0.76198 | 1.0708 |  | CHECK SUM |  | 1.3896 | -0.067448 | 0.69401 | 0.40573 | 0.077344 | 1.1855 | -0.31914 | CHECK SUM |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CHECK SUM |  | -0.21224 | -0.57565 | 1.15 | -0.35208 | -0.23372 | 1.3591 | -0.25391
|  |  | -0.75182 | 0.69479 | 0.92591 | -0.16589 | -0.03099 | 0.7901 | 0.33685 |  |  |  | 0.66654 | 0.18372 | 1.2663 | -0.75026 | -0.28242 | 0.93047 | -0.20443 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.02526 | -0.53372 | 1.2682 | 0.45612 | -0.69154 | 0.25625 | 1.2534
|  |  | 0.092969 | -0.9099 | -0.51719 | -0.46589 | -0.60794 | 0.46745 | 0.21419 |  |  |  | 0.99948 | 0.7901 | 0.20573 | 0.79102 | 0.9526 | 0.24349 | -0.79323 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | -1.018 | 0.60573 | 1.2572 | 1.2286 | -0.87031 | 0.90599 | -0.1418
|  |  | -0.24922 | -0.0071615 | -0.59883 | -0.97865 | 1.2408 | -0.82513 | 1.4171 |  |  |  | -0.41979 | 0.81211 | -0.59609 | -1.1576 | 0.7043 | -0.44258 | 0.95742 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | -0.29414 | 0.15065 | -0.035547 | 0.66354 | 1.3793 | 0.32526 | -0.44896
|  |  | 0.27552 | 0.41771 | 1.0719 | 1.3509 | 0.95365 | -0.10768 | -0.21042 |  |  |  | 0.14362 | -0.3556 | 0.35156 | 0.90573 | 0.48503 | 1.1363 | -0.47461 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.19779 | -0.66211 | -0.93919 | -0.98594 | 1.2684 | 0.57383 | 1.4648

## Balometer 120
All measurments without backpressure correction
| 2023-12-11 |  | 2023-12-16
| All open |  | All open, 102kw |  |  | AVERAGE | Time | Upstairs closed |  |  | AVERAGE | Time | Upstairs closed |  |  | AVERAGE | Time
| ERV OFF | ERV On | ERV off | ERV off | ERV off | ERV OFF |  | ERV off | ERV off | ERV off | ERV OFF |  | ERV on | ERV on | ERV on | ERV on
Office by lights | 36 | 44 | 27 | 42 | 27 | 32 | 8:05 | 41 | 41 | 42 | 41.3333 | 11:08 | 43 | 39 | 40 | 40.6667 | 11:35
Dining Room over table | 39 | 41 | 25 | 27 | 29 | 27 | 7:56 | 43 | 43 | 43 | 43 | 11:11 | 33 | 32 | 36 | 33.6667 | 11:37
Living Room | 46 | 45 | 44 | 47 | 46 | 45.6667 | 7:59 | 51 | 51 | 50 | 50.6667 | 11:05 | 50 | 51 | 50 | 50.3333 | 11:39
Guest | 51 | 56 | 47 | 49 | 48 | 48 | 8:02 | 52 | 52 | 52 | 52 | 11:15 | 53 | 53 | 52 | 52.6667 | 11:24
Bath by window | 62 | 63 | 72 | 72 | 72 | 72 | 8:07 | 69 | 68 | 69 | 68.6667 | 11:20 | 72 | 74 | 73 | 73 | 11:26
Kitchen | 60 | 63 | 63 | 64 | 64 | 63.6667 | 7:52 | 68 | 71 | 70 | 69.6667 | 11:12 | 71 | 73 | 74 | 72.6667 | 11:40
Bedroom by back window | 92 | 92 | 99 | 101 | 99 | 99.6667 | 8:10 | 104 | 106 | 105 | 105 | 11:22 | 105 | 110 | 106 | 107 | 11:33
Upstairs under desk (EST)* |  |  | 57.6936 | 55.1007 | 55.1007 | 55.965 | 8:50 | 18.0448 | 19.3981 | 18.947 | 18.7967 | est | 24.8116 | 25.2627 | 25.2627 | 25.1123 | 9:45
Near handler upstairs | 91 | 94 | 76 | 77 | 77 | 76.6667 | 8:18 | 46 | 42 | 42 | 43.3333 | 9:23 | 50 | 52 | 51 | 51 | 9:33
Upstairs bath over sink | 62 | 69 | 56 | 55 | 46 | 52.3333 | 8:21 | 33 | 32 | 29 | 31.3333 | 9:26 | 26 | 25 | 26 | 25.6667 | 9:39
Upstairs bedroom | 46 | 48 | 89 | 85 | 85 | 86.3333 | 8:27 | 40 | 43 | 42 | 41.6667 | 9:29 | 55 | 56 | 56 | 55.6667 | 9:36
All ducts | 585 | 615 | 655.6936 | 674.1007 | 648.1007 | 659.2983 | ERV on? | 565.0448 | 568.3981 | 562.947 | 565.4633 |  | 582.8116 | 590.2627 | 589.2627 | 587.4457 |  | 1.0389
Upstairs ducts | 386 | 404 | 377 | 402 | 385 | 388 |  | 428 | 432 | 431 | 430.3333 |  | 427 | 432 | 431 | 430
*Estimation for inaccessible event using
Hot wire anemometer flush/aligned with grill |  |  | Q | C | Q | [7 empty] | Q | C | Q
Upstairs under desk | high |  | 264 | 245 | 214 | 196.7778 | 8:50 | [5 empty] | 19 | 30 | 42 | 91.7778 | 9:45
| med |  | 233 | 124 | 226 | [7 empty] | 40 | 31 | 26
| low |  | 174 | 96 | 195 | [7 empty] | 226 | 246 | 166
Upstairs bedroom | high |  | 730 | 488 | 333 | 303.5556 | [6 empty] | 110 | 23 | 81 | 203.4444 | 9:50
| med |  | 442 | 308 | 122 | [7 empty] | 51 | 49 | 44
| low |  | 186 | 41 | 82 | [7 empty] | 439 | 384 | 650
Upstairs closed
Both doors closed
All 4 upstairs louvres closed for HC supply
HC Return open, ERV Open

## Traverse 120
Three axis traverse: Opposite measurements in equal area rings | [5 empty] | Interior cross section |  | 0.7854
12 inch cylindrical duct; five ring
https://tsi.com/getmedia/1a11d344-0a58-4ca6-94fe-65721825686b/AF-106%20Traversing%20a%20Duct?ext=.pdf
| TSI; | 0.019 | 0.077 | 0.153 | 0.217 | 0.361 | 0.639 | 0.783 | 0.847 | 0.923 | 0.981 | [7 empty] | 0 axis
| 12 | 0.228 | 0.924 | 1.836 | 2.604 | 4.332 | 7.668 | 9.396 | 10.164 | 11.076 | 11.772 |  |  | 60 axis |  |  |  |  | 941 |  |  |  |  | 120 axis
| 0.5 | 0.728 | 1.424 | 2.336 | 3.104 | 4.832 | 8.168 | 9.896 | 10.664 | 11.576 | 12.272 |  |  | 622 |  |  |  |  | 979 |  |  |  |  | 703
Upstairs closed, ERV Off | [14 empty] | 640 |  |  |  | 1036 |  |  |  | 867
0.5 | 0 | 941 | 979 | 1036 | 987 | 1060 | 886 | 1098 | 907 | 1042 | 826 | fpm | 15 second measurements |  |  | 381 |  |  | 987 |  |  | 910
0 | 60 | 622 | 640 | 381 | 445 | 601 | 827 | 820 | 801 | 775 | 655 | fpm |  |  |  |  | 445 |  | 1060 |  | 916
0 | 120 | 649 | 530 | 383 | 316 | 388 | 920 | 916 | 910 | 867 | 703 | fpm | [5 empty] | 601 |  | 920
[11 empty] | 763.7 | fpm average | [5 empty] | 388 |  | 827
| 2023-12-16 | start time: 1:05 pm (100-101 watts) |  |  |  | One hour average 100.4 |  |  |  |  | 599.8086 | cfm average |  |  |  |  | 316 |  | 886 |  | 820
|  | finish time: 2:05 | [13 empty] | 383 |  |  | 1098 |  |  | 801
Upstairs closed, ERV On | [14 empty] | 530 |  |  |  | 907 |  |  |  | 775
0,5 | 0 | 813 | 929 | 954 | 916 | 886 | 874 | 941 | 863 | 911 | 909 |  | 15 second measurements | 649 |  |  |  |  | 1042 |  |  |  |  | 655
0.5 | 60 | 451 | 695 | 580 | 545 | 938 | 818 | 970 | 900 | 861 | 736 | [7 empty] | 826
0.5 | 120 | 435 | 501 | 270 | 386 | 781 | 875 | 903 | 932 | 915 | 438
[11 empty] | 764.2 | fpm average | [6 empty] | 813
|  | start time: 2:58 pm |  | 103-104 watts |  | One hour average 102.9 |  |  |  |  | 600.2013 | cfm average |  | 451 |  |  |  |  | 929 |  |  |  |  | 438
|  | finish time: | 4:24pm | [11 empty] | 685 |  |  |  | 954 |  |  |  | 915
[16 empty] | 580 |  |  | 916 |  |  | 932
[17 empty] | 545 |  | 886 |  | 903
|  | Note that 120 degrees far cell may be obstructed by flange, but difference in ERV/no ERV measurement is repeatable. | [15 empty] | 938 |  | 875
[18 empty] | 781 |  | 818
[17 empty] | 386 |  | 874 |  | 970
[16 empty] | 270 |  |  | 941 |  |  | 900
[15 empty] | 501 |  |  |  | 863 |  |  |  | 861
[14 empty] | 435 |  |  |  |  | 911 |  |  |  |  | 736
Using the anemometer measurement -- did internal diameter check with tape: appears to be very close to 12" interior diameter even within flange, possiby slighly above | [18 empty] | 909
Flange is not very different from rest of pipe -- looks almost flush. Measurements were on the flange
Bends within flange grab at most a couple of inches
Net is something very close to a perfect 12" diameter

## Fan voltage histograms
120 all minutes |  | 118 Subpanel-Heat Pump-118 AH A (kWatts) | 118 Subpanel-Heat Pump-118 AH B (kWatts)
0.111 | 111 | 0.0471 | 0.0484 | 96
0.1107 | 111 | 0.0474 | 0.0486 | 96
0.1107 | 111 | 0.0473 | 0.0482 | 96
0.1107 | 111 | 0.0472 | 0.0483 | 96
0.1106 | 111 | 0.0474 | 0.0484 | 96
0.1105 | 111 | 0.0475 | 0.0483 | 96
0.1105 | 111 | 0.0472 | 0.0483 | 96
0.1104 | 110 | 0.0469 | 0.0476 | 95
0.1104 | 110 | 0.0468 | 0.0477 | 95
0.1103 | 110 | 0.047 | 0.0479 | 95
0.1103 | 110 | 0.0469 | 0.0477 | 95
0.1103 | 110 | 0.0469 | 0.0479 | 95
0.1102 | 110 | 0.047 | 0.0476 | 95
0.1101 | 110 | 0.0469 | 0.0476 | 95
0.1101 | 110 | 0.047 | 0.0478 | 95
0.1101 | 110 | 0.0469 | 0.0476 | 95
0.1101 | 110 | 0.0468 | 0.0478 | 95
0.1101 | 110 | 0.0469 | 0.0476 | 95
0.11 | 110 | 0.0468 | 0.0477 | 95
0.11 | 110 | 0.0468 | 0.0477 | 95 | 15030
0.1099 | 110 | 0.047 | 0.0478 | 95
0.1099 | 110 | 0.0468 | 0.0477 | 95
0.1099 | 110 | 0.0469 | 0.0477 | 95
0.1098 | 110 | 0.047 | 0.0477 | 95
0.1098 | 110 | 0.0469 | 0.0476 | 95
0.1098 | 110 | 0.0469 | 0.0478 | 95
0.1097 | 110 | 0.0469 | 0.0476 | 95
0.1097 | 110 | 0.0468 | 0.0478 | 95
0.1097 | 110 | 0.0469 | 0.0476 | 95
0.1096 | 110 | 0.0469 | 0.0476 | 95
0.1096 | 110 | 0.0468 | 0.0477 | 95
0.1096 | 110 | 0.0468 | 0.0477 | 95
0.1096 | 110 | 0.0468 | 0.0477 | 95
0.1095 | 110 | 0.0469 | 0.0476 | 95
0.1095 | 110 | 0.047 | 0.0476 | 95
0.1094 | 109 | 0.0468 | 0.0477 | 95
0.1094 | 109 | 0.0468 | 0.0477 | 95
0.1094 | 109 | 0.0468 | 0.0477 | 95
0.1094 | 109 | 0.0469 | 0.0476 | 95
0.1093 | 109 | 0.0468 | 0.0477 | 95
0.1093 | 109 | 0.0469 | 0.0476 | 95
0.1092 | 109 | 0.0468 | 0.0477 | 95
0.1092 | 109 | 0.0469 | 0.0476 | 95
0.1092 | 109 | 0.047 | 0.0476 | 95
0.1092 | 109 | 0.0469 | 0.0476 | 95
0.1091 | 109 | 0.047 | 0.0477 | 95
0.109 | 109 | 0.0469 | 0.0477 | 95
0.1089 | 109 | 0.0469 | 0.0476 | 95
0.1088 | 109 | 0.047 | 0.0476 | 95
0.1087 | 109 | 0.047 | 0.0476 | 95
0.1086 | 109 | 0.047 | 0.0477 | 95
0.1086 | 109 | 0.047 | 0.0478 | 95
0.1085 | 109 | 0.047 | 0.0477 | 95
0.1085 | 109 | 0.047 | 0.0477 | 95
0.1085 | 109 | 0.0469 | 0.0477 | 95
0.1085 | 109 | 0.0469 | 0.0476 | 95
0.1085 | 109 | 0.0469 | 0.0477 | 95
0.1085 | 109 | 0.0469 | 0.0476 | 95
0.1085 | 109 | 0.0471 | 0.0483 | 95
0.1084 | 108 | 0.047 | 0.0482 | 95
0.1084 | 108 | 0.0471 | 0.0483 | 95
0.1084 | 108 | 0.0471 | 0.0482 | 95
0.1083 | 108 | 0.047 | 0.0481 | 95
0.1083 | 108 | 0.0471 | 0.048 | 95
0.1083 | 108 | 0.047 | 0.0481 | 95
0.1083 | 108 | 0.0469 | 0.048 | 95
0.1083 | 108 | 0.047 | 0.0482 | 95
0.1083 | 108 | 0.047 | 0.0481 | 95
0.1082 | 108 | 0.047 | 0.0479 | 95
0.1082 | 108 | 0.047 | 0.0481 | 95
0.1082 | 108 | 0.0467 | 0.0478 | 95
0.1082 | 108 | 0.0468 | 0.048 | 95
0.1081 | 108 | 0.0469 | 0.048 | 95
0.1081 | 108 | 0.0469 | 0.048 | 95
0.1081 | 108 | 0.0468 | 0.0477 | 95
0.108 | 108 | 0.0469 | 0.0482 | 95
0.108 | 108 | 0.047 | 0.048 | 95
0.1079 | 108 | 0.047 | 0.048 | 95
0.1078 | 108 | 0.0468 | 0.048 | 95
0.1078 | 108 | 0.047 | 0.0481 | 95
0.1077 | 108 | 0.0468 | 0.0478 | 95
0.1074 | 107 | 0.047 | 0.0481 | 95
0.1073 | 107 | 0.0469 | 0.048 | 95
0.1072 | 107 | 0.0468 | 0.048 | 95
0.1072 | 107 | 0.0468 | 0.0478 | 95
0.1071 | 107 | 0.0468 | 0.0478 | 95
0.1071 | 107 | 0.0468 | 0.0477 | 95
0.1071 | 107 | 0.0467 | 0.0479 | 95
0.1071 | 107 | 0.0469 | 0.048 | 95
0.1071 | 107 | 0.0469 | 0.0479 | 95
0.107 | 107 | 0.047 | 0.0479 | 95
0.107 | 107 | 0.0469 | 0.0478 | 95
0.1069 | 107 | 0.0471 | 0.048 | 95
0.1069 | 107 | 0.0467 | 0.0478 | 95
0.1069 | 107 | 0.0468 | 0.0479 | 95
0.1068 | 107 | 0.0468 | 0.0478 | 95
0.1068 | 107 | 0.0469 | 0.048 | 95
0.1068 | 107 | 0.0468 | 0.0479 | 95
0.1068 | 107 | 0.0468 | 0.0478 | 95
0.1067 | 107 | 0.0467 | 0.0479 | 95
0.1067 | 107 | 0.0467 | 0.0478 | 95
0.1067 | 107 | 0.0467 | 0.0479 | 95
0.1067 | 107 | 0.0467 | 0.0478 | 95
0.1067 | 107 | 0.0467 | 0.0479 | 95
0.1067 | 107 | 0.0467 | 0.0478 | 95
0.1067 | 107 | 0.0467 | 0.0478 | 95
0.1067 | 107 | 0.0466 | 0.0479 | 95
0.1066 | 107 | 0.0467 | 0.048 | 95
0.1066 | 107 | 0.0468 | 0.0478 | 95
0.1066 | 107 | 0.0468 | 0.0477 | 95
0.1066 | 107 | 0.0468 | 0.0477 | 95
0.1066 | 107 | 0.0467 | 0.0478 | 95
0.1066 | 107 | 0.0468 | 0.0478 | 95
0.1066 | 107 | 0.0468 | 0.0479 | 95
0.1066 | 107 | 0.0468 | 0.0479 | 95
0.1066 | 107 | 0.0468 | 0.0479 | 95
0.1066 | 107 | 0.0467 | 0.0478 | 95
0.1065 | 107 | 0.0467 | 0.0478 | 95
0.1065 | 107 | 0.0467 | 0.0479 | 95
0.1065 | 107 | 0.0468 | 0.0478 | 95
0.1065 | 107 | 0.0467 | 0.0479 | 95
0.1065 | 107 | 0.0468 | 0.0479 | 95
0.1065 | 107 | 0.0467 | 0.0478 | 95
0.1065 | 107 | 0.0468 | 0.0477 | 95
0.1065 | 107 | 0.0468 | 0.0478 | 95
0.1065 | 107 | 0.0467 | 0.0478 | 95
0.1065 | 107 | 0.0468 | 0.0477 | 95
0.1065 | 107 | 0.0469 | 0.0478 | 95
0.1065 | 107 | 0.0467 | 0.0478 | 95
0.1065 | 107 | 0.0472 | 0.0482 | 95
0.1065 | 107 | 0.0472 | 0.0481 | 95
0.1064 | 106 | 0.0472 | 0.0479 | 95
0.1064 | 106 | 0.0473 | 0.048 | 95
0.1064 | 106 | 0.0473 | 0.0481 | 95
0.1064 | 106 | 0.0471 | 0.0479 | 95
0.1064 | 106 | 0.0472 | 0.0482 | 95
0.1064 | 106 | 0.047 | 0.0481 | 95
0.1064 | 106 | 0.0472 | 0.0481 | 95
0.1064 | 106 | 0.0472 | 0.0481 | 95
0.1064 | 106 | 0.0471 | 0.0481 | 95
0.1064 | 106 | 0.0472 | 0.048 | 95
0.1064 | 106 | 0.0471 | 0.0479 | 95
0.1064 | 106 | 0.0472 | 0.0481 | 95
0.1064 | 106 | 0.047 | 0.0479 | 95
0.1064 | 106 | 0.047 | 0.0478 | 95
0.1064 | 106 | 0.0471 | 0.0479 | 95
0.1064 | 106 | 0.0471 | 0.048 | 95
0.1064 | 106 | 0.0471 | 0.0481 | 95
0.1064 | 106 | 0.047 | 0.0478 | 95
0.1064 | 106 | 0.047 | 0.0478 | 95
0.1064 | 106 | 0.0469 | 0.0479 | 95
0.1064 | 106 | 0.0472 | 0.048 | 95
0.1064 | 106 | 0.0471 | 0.0482 | 95
0.1064 | 106 | 0.0469 | 0.0478 | 95
0.1064 | 106 | 0.0471 | 0.0479 | 95
0.1064 | 106 | 0.047 | 0.0479 | 95
0.1064 | 106 | 0.047 | 0.0478 | 95
0.1063 | 106 | 0.0469 | 0.0479 | 95
0.1063 | 106 | 0.0472 | 0.0481 | 95
0.1063 | 106 | 0.0471 | 0.0479 | 95
0.1063 | 106 | 0.047 | 0.0478 | 95
0.1063 | 106 | 0.0471 | 0.0479 | 95
0.1063 | 106 | 0.047 | 0.048 | 95
0.1063 | 106 | 0.0471 | 0.0479 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0471 | 0.0479 | 95
0.1063 | 106 | 0.0469 | 0.048 | 95
0.1063 | 106 | 0.047 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0477 | 95
0.1063 | 106 | 0.047 | 0.0479 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0469 | 0.0479 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0469 | 0.0479 | 95
0.1063 | 106 | 0.0471 | 0.048 | 95
0.1063 | 106 | 0.0469 | 0.0478 | 95
0.1063 | 106 | 0.047 | 0.048 | 95
0.1063 | 106 | 0.047 | 0.0478 | 95
0.1063 | 106 | 0.0469 | 0.0478 | 95
0.1063 | 106 | 0.047 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0477 | 95
0.1063 | 106 | 0.0468 | 0.0477 | 95
0.1063 | 106 | 0.0468 | 0.0477 | 95
0.1063 | 106 | 0.0468 | 0.0477 | 95
0.1063 | 106 | 0.0467 | 0.0478 | 95
0.1063 | 106 | 0.0467 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0479 | 95
0.1063 | 106 | 0.0467 | 0.0478 | 95
0.1063 | 106 | 0.0469 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0479 | 95
0.1063 | 106 | 0.0467 | 0.0479 | 95
0.1063 | 106 | 0.0469 | 0.0479 | 95
0.1063 | 106 | 0.0468 | 0.048 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0478 | 95
0.1063 | 106 | 0.0469 | 0.0477 | 95
0.1063 | 106 | 0.0469 | 0.0478 | 95
0.1063 | 106 | 0.0468 | 0.0479 | 95
0.1062 | 106 | 0.0469 | 0.048 | 95
0.1062 | 106 | 0.0471 | 0.0481 | 95
0.1062 | 106 | 0.0467 | 0.0478 | 95
0.1062 | 106 | 0.0471 | 0.048 | 95
0.1062 | 106 | 0.0471 | 0.0481 | 95
0.1062 | 106 | 0.047 | 0.0481 | 95
0.1062 | 106 | 0.047 | 0.0482 | 95
0.1062 | 106 | 0.0471 | 0.0481 | 95
0.1062 | 106 | 0.0471 | 0.0481 | 95
0.1062 | 106 | 0.0471 | 0.0479 | 95
0.1062 | 106 | 0.047 | 0.048 | 95
0.1062 | 106 | 0.047 | 0.0479 | 95
0.1062 | 106 | 0.047 | 0.0482 | 95
0.1062 | 106 | 0.0469 | 0.0481 | 95
0.1062 | 106 | 0.0468 | 0.048 | 95
0.1062 | 106 | 0.0471 | 0.048 | 95
0.1062 | 106 | 0.0469 | 0.048 | 95
0.1062 | 106 | 0.0473 | 0.048 | 95
0.1062 | 106 | 0.0472 | 0.0481 | 95
0.1062 | 106 | 0.0472 | 0.0482 | 95
0.1062 | 106 | 0.0471 | 0.0481 | 95
0.1062 | 106 | 0.0472 | 0.048 | 95
0.1062 | 106 | 0.0471 | 0.0479 | 95
0.1062 | 106 | 0.047 | 0.0478 | 95
0.1062 | 106 | 0.0468 | 0.0479 | 95
0.1062 | 106 | 0.0473 | 0.0481 | 95
0.1062 | 106 | 0.0469 | 0.0479 | 95
0.1062 | 106 | 0.0469 | 0.0479 | 95
0.1062 | 106 | 0.0473 | 0.048 | 95
0.1062 | 106 | 0.0472 | 0.048 | 95
0.1062 | 106 | 0.0472 | 0.0482 | 95
0.1062 | 106 | 0.0471 | 0.048 | 95
0.1062 | 106 | 0.0472 | 0.0482 | 95
0.1062 | 106 | 0.0472 | 0.0479 | 95
0.1062 | 106 | 0.0472 | 0.048 | 95
0.1062 | 106 | 0.047 | 0.0479 | 95
0.1062 | 106 | 0.0471 | 0.0481 | 95
0.1062 | 106 | 0.0468 | 0.0477 | 95
0.1062 | 106 | 0.0469 | 0.0477 | 95
0.1062 | 106 | 0.0469 | 0.0477 | 95
0.1062 | 106 | 0.0468 | 0.0477 | 95
0.1062 | 106 | 0.0468 | 0.0479 | 95
0.1062 | 106 | 0.0469 | 0.0479 | 95
0.1062 | 106 | 0.0469 | 0.0479 | 95
0.1062 | 106 | 0.0469 | 0.0478 | 95
0.1062 | 106 | 0.0468 | 0.0477 | 95
0.1062 | 106 | 0.0468 | 0.0479 | 95
0.1062 | 106 | 0.0469 | 0.0476 | 95
0.1061 | 106 | 0.0469 | 0.0476 | 95
0.1061 | 106 | 0.0469 | 0.0478 | 95
0.1061 | 106 | 0.0467 | 0.0479 | 95
0.1061 | 106 | 0.0468 | 0.0478 | 95
0.1061 | 106 | 0.0468 | 0.0478 | 95
0.1061 | 106 | 0.0468 | 0.0479 | 95
0.1061 | 106 | 0.047 | 0.0482 | 95
0.1061 | 106 | 0.047 | 0.048 | 95
0.1061 | 106 | 0.047 | 0.0481 | 95
0.1061 | 106 | 0.047 | 0.0478 | 95
0.1061 | 106 | 0.0469 | 0.048 | 95
0.1061 | 106 | 0.0471 | 0.0479 | 95
0.1061 | 106 | 0.0472 | 0.0481 | 95
0.1061 | 106 | 0.047 | 0.048 | 95
0.1061 | 106 | 0.0469 | 0.0478 | 95
0.1061 | 106 | 0.0469 | 0.0478 | 95
0.1061 | 106 | 0.0467 | 0.0478 | 95
0.1061 | 106 | 0.047 | 0.048 | 95
0.1061 | 106 | 0.047 | 0.0478 | 95
0.1061 | 106 | 0.0469 | 0.0476 | 95
0.1061 | 106 | 0.047 | 0.0479 | 95
0.1061 | 106 | 0.0468 | 0.0477 | 95
0.1061 | 106 | 0.0468 | 0.0479 | 95
0.1061 | 106 | 0.0467 | 0.0478 | 95
0.1061 | 106 | 0.0467 | 0.0479 | 95
0.1061 | 106 | 0.0469 | 0.0477 | 95
0.1061 | 106 | 0.0467 | 0.0478 | 95
0.1061 | 106 | 0.0468 | 0.0479 | 95
0.1061 | 106 | 0.0468 | 0.0477 | 95
0.1061 | 106 | 0.0469 | 0.0476 | 95
0.1061 | 106 | 0.0469 | 0.0479 | 95
0.1061 | 106 | 0.0468 | 0.0478 | 95
0.1061 | 106 | 0.0469 | 0.0477 | 95
0.1061 | 106 | 0.0468 | 0.0477 | 95
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0467 | 0.0474 | 94
0.1061 | 106 | 0.0467 | 0.0473 | 94
0.1061 | 106 | 0.0467 | 0.0475 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0467 | 0.0475 | 94
0.1061 | 106 | 0.0467 | 0.0476 | 94
0.1061 | 106 | 0.0467 | 0.0475 | 94
0.1061 | 106 | 0.0466 | 0.0474 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0468 | 0.0474 | 94
0.1061 | 106 | 0.0467 | 0.0477 | 94
0.1061 | 106 | 0.0469 | 0.0475 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0469 | 0.0474 | 94
0.1061 | 106 | 0.0469 | 0.0475 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0466 | 0.0475 | 94
0.1061 | 106 | 0.0467 | 0.0475 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0468 | 0.0476 | 94
0.1061 | 106 | 0.0467 | 0.0474 | 94
0.1061 | 106 | 0.0468 | 0.0475 | 94
0.1061 | 106 | 0.0467 | 0.0476 | 94
0.1061 | 106 | 0.0466 | 0.0476 | 94
0.1061 | 106 | 0.0467 | 0.0476 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0466 | 0.0475 | 94
0.106 | 106 | 0.0466 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0467 | 0.0476 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0466 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0466 | 0.0476 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0466 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0476 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0476 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0466 | 0.0476 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0466 | 0.0474 | 94
0.106 | 106 | 0.0467 | 0.0477 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0468 | 0.0474 | 94
0.106 | 106 | 0.0465 | 0.0474 | 94
0.106 | 106 | 0.0467 | 0.0474 | 94
0.106 | 106 | 0.0467 | 0.0475 | 94
0.106 | 106 | 0.0465 | 0.0474 | 94
0.106 | 106 | 0.0466 | 0.0474 | 94
0.1059 | 106 | 0.0466 | 0.0474 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0465 | 0.0474 | 94
0.1059 | 106 | 0.0466 | 0.0475 | 94
0.1059 | 106 | 0.0466 | 0.0474 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0466 | 0.0475 | 94
0.1059 | 106 | 0.0466 | 0.0474 | 94
0.1059 | 106 | 0.0467 | 0.0473 | 94
0.1059 | 106 | 0.0466 | 0.0474 | 94
0.1059 | 106 | 0.0467 | 0.0476 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0466 | 0.0476 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0467 | 0.0473 | 94
0.1059 | 106 | 0.0466 | 0.0474 | 94
0.1059 | 106 | 0.0466 | 0.0475 | 94
0.1059 | 106 | 0.0465 | 0.0474 | 94
0.1059 | 106 | 0.0467 | 0.0475 | 94
0.1059 | 106 | 0.0465 | 0.0475 | 94
0.1059 | 106 | 0.0466 | 0.0475 | 94
0.1058 | 106 | 0.0468 | 0.0475 | 94
0.1058 | 106 | 0.0467 | 0.0474 | 94
0.1058 | 106 | 0.0465 | 0.0475 | 94
0.1058 | 106 | 0.0467 | 0.0475 | 94
0.1058 | 106 | 0.0467 | 0.0475 | 94
0.1058 | 106 | 0.0465 | 0.0472 | 94
0.1058 | 106 | 0.0466 | 0.0474 | 94
0.1058 | 106 | 0.0468 | 0.0476 | 94
0.1058 | 106 | 0.0467 | 0.0476 | 94
0.1058 | 106 | 0.0468 | 0.0475 | 94
0.1058 | 106 | 0.0469 | 0.0475 | 94
0.1058 | 106 | 0.0468 | 0.0476 | 94
0.1058 | 106 | 0.0468 | 0.0476 | 94
0.1058 | 106 | 0.0467 | 0.0476 | 94
0.1058 | 106 | 0.0467 | 0.0476 | 94
0.1058 | 106 | 0.0468 | 0.0476 | 94
0.1058 | 106 | 0.0466 | 0.0475 | 94
0.1058 | 106 | 0.0467 | 0.0476 | 94
0.1058 | 106 | 0.0468 | 0.0475 | 94
0.1058 | 106 | 0.0467 | 0.0476 | 94
0.1057 | 106 | 0.0468 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0474 | 94
0.1057 | 106 | 0.0466 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0476 | 94
0.1057 | 106 | 0.0468 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0467 | 0.0473 | 94
0.1057 | 106 | 0.0469 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0467 | 0.0476 | 94
0.1057 | 106 | 0.0468 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0476 | 94
0.1057 | 106 | 0.0468 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0475 | 94
0.1057 | 106 | 0.0467 | 0.0476 | 94
0.1057 | 106 | 0.0468 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0475 | 94
0.1057 | 106 | 0.0466 | 0.0474 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0468 | 0.0475 | 94
0.1057 | 106 | 0.0466 | 0.0475 | 94
0.1057 | 106 | 0.0467 | 0.0475 | 94
0.1057 | 106 | 0.0467 | 0.0476 | 94
0.1057 | 106 | 0.0467 | 0.0476 | 94
0.1056 | 106 | 0.0466 | 0.0474 | 94
0.1056 | 106 | 0.0468 | 0.0475 | 94
0.1056 | 106 | 0.0465 | 0.0475 | 94
0.1056 | 106 | 0.0467 | 0.0475 | 94
0.1056 | 106 | 0.0467 | 0.0475 | 94
0.1056 | 106 | 0.0467 | 0.0473 | 94
0.1056 | 106 | 0.0468 | 0.0475 | 94
0.1056 | 106 | 0.0469 | 0.0474 | 94
0.1056 | 106 | 0.0466 | 0.0475 | 94
0.1056 | 106 | 0.0467 | 0.0475 | 94
0.1056 | 106 | 0.0466 | 0.0473 | 94
0.1056 | 106 | 0.0465 | 0.0474 | 94
0.1056 | 106 | 0.0467 | 0.0474 | 94
0.1056 | 106 | 0.0467 | 0.0476 | 94
0.1056 | 106 | 0.0469 | 0.0475 | 94
0.1056 | 106 | 0.0468 | 0.0476 | 94
0.1056 | 106 | 0.0466 | 0.0474 | 94
0.1056 | 106 | 0.0468 | 0.0474 | 94
0.1056 | 106 | 0.0469 | 0.0475 | 94
0.1056 | 106 | 0.0467 | 0.0477 | 94
0.1056 | 106 | 0.0467 | 0.0477 | 94
0.1056 | 106 | 0.0468 | 0.0475 | 94
0.1056 | 106 | 0.0467 | 0.0475 | 94
0.1056 | 106 | 0.0468 | 0.0474 | 94
0.1056 | 106 | 0.0468 | 0.0476 | 94
0.1056 | 106 | 0.0469 | 0.0475 | 94
0.1056 | 106 | 0.0468 | 0.0475 | 94
0.1056 | 106 | 0.0468 | 0.0476 | 94
0.1056 | 106 | 0.0468 | 0.0473 | 94
0.1056 | 106 | 0.0465 | 0.0474 | 94
0.1056 | 106 | 0.0469 | 0.0474 | 94
0.1056 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0468 | 0.0475 | 94
0.1055 | 106 | 0.0467 | 0.0475 | 94
0.1055 | 106 | 0.0467 | 0.0473 | 94
0.1055 | 106 | 0.0466 | 0.0474 | 94
0.1055 | 106 | 0.0466 | 0.0472 | 94
0.1055 | 106 | 0.0466 | 0.0475 | 94
0.1055 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0466 | 0.0475 | 94
0.1055 | 106 | 0.0467 | 0.0475 | 94
0.1055 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0466 | 0.0473 | 94
0.1055 | 106 | 0.0466 | 0.0474 | 94
0.1055 | 106 | 0.0465 | 0.0474 | 94
0.1055 | 106 | 0.0465 | 0.0474 | 94
0.1055 | 106 | 0.0467 | 0.0475 | 94
0.1055 | 106 | 0.0466 | 0.0474 | 94
0.1055 | 106 | 0.0464 | 0.0473 | 94
0.1055 | 106 | 0.0468 | 0.0476 | 94
0.1055 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0467 | 0.0473 | 94
0.1055 | 106 | 0.0466 | 0.0475 | 94
0.1055 | 106 | 0.0466 | 0.0474 | 94
0.1055 | 106 | 0.0466 | 0.0473 | 94
0.1055 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0467 | 0.0473 | 94
0.1055 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0467 | 0.0473 | 94
0.1055 | 106 | 0.0465 | 0.0472 | 94
0.1055 | 106 | 0.0468 | 0.0474 | 94
0.1055 | 106 | 0.0467 | 0.0474 | 94
0.1055 | 106 | 0.0466 | 0.0477 | 94
0.1055 | 106 | 0.0467 | 0.0477 | 94
0.1055 | 106 | 0.0467 | 0.0477 | 94
0.1055 | 106 | 0.0464 | 0.0477 | 94
0.1055 | 106 | 0.0466 | 0.0477 | 94
0.1055 | 106 | 0.0466 | 0.0477 | 94
0.1055 | 106 | 0.0466 | 0.0476 | 94
0.1055 | 106 | 0.0466 | 0.0477 | 94
0.1055 | 106 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0475 | 94
0.1054 | 105 | 0.0464 | 0.0475 | 94
0.1054 | 105 | 0.0467 | 0.0476 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0478 | 94
0.1054 | 105 | 0.0466 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0477 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0478 | 94
0.1054 | 105 | 0.0464 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0478 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0478 | 94
0.1054 | 105 | 0.0465 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0476 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0475 | 94
0.1054 | 105 | 0.0466 | 0.0478 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0475 | 94
0.1054 | 105 | 0.0464 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0478 | 94
0.1054 | 105 | 0.0465 | 0.0477 | 94
0.1054 | 105 | 0.0467 | 0.0476 | 94
0.1054 | 105 | 0.0465 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0467 | 0.0476 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0476 | 94
0.1054 | 105 | 0.0465 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0477 | 94
0.1054 | 105 | 0.0465 | 0.0476 | 94
0.1054 | 105 | 0.0467 | 0.0477 | 94
0.1054 | 105 | 0.0466 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0476 | 94
0.1054 | 105 | 0.0464 | 0.0476 | 94
0.1054 | 105 | 0.0466 | 0.0478 | 94
0.1054 | 105 | 0.0467 | 0.0476 | 94
0.1053 | 105 | 0.0466 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0466 | 0.0477 | 94
0.1053 | 105 | 0.0466 | 0.0476 | 94
0.1053 | 105 | 0.0466 | 0.0474 | 94
0.1053 | 105 | 0.0464 | 0.0478 | 94
0.1053 | 105 | 0.0466 | 0.0477 | 94
0.1053 | 105 | 0.0466 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0464 | 0.0476 | 94
0.1053 | 105 | 0.0466 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0467 | 0.0477 | 94
0.1053 | 105 | 0.0466 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0466 | 0.0478 | 94
0.1053 | 105 | 0.0466 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0475 | 94
0.1053 | 105 | 0.0467 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0466 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0478 | 94
0.1053 | 105 | 0.0466 | 0.0475 | 94
0.1053 | 105 | 0.0464 | 0.0475 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0464 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0474 | 94
0.1053 | 105 | 0.0464 | 0.0479 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0467 | 0.0475 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1053 | 105 | 0.0464 | 0.0477 | 94
0.1053 | 105 | 0.0465 | 0.0477 | 94
0.1053 | 105 | 0.0466 | 0.0476 | 94
0.1053 | 105 | 0.0465 | 0.0476 | 94
0.1052 | 105 | 0.0465 | 0.0477 | 94
0.1052 | 105 | 0.0466 | 0.0478 | 94
0.1052 | 105 | 0.0464 | 0.0476 | 94
0.1052 | 105 | 0.0464 | 0.0475 | 94
0.1052 | 105 | 0.0464 | 0.0476 | 94
0.1052 | 105 | 0.0466 | 0.0478 | 94
0.1052 | 105 | 0.0464 | 0.0477 | 94
0.1052 | 105 | 0.0466 | 0.0475 | 94
0.1052 | 105 | 0.0466 | 0.0477 | 94
0.1052 | 105 | 0.0466 | 0.0475 | 94
0.1052 | 105 | 0.0463 | 0.0476 | 94
0.1052 | 105 | 0.0464 | 0.0477 | 94
0.1052 | 105 | 0.0464 | 0.0477 | 94
0.1052 | 105 | 0.0464 | 0.0474 | 94
0.1052 | 105 | 0.0467 | 0.0477 | 94
0.1052 | 105 | 0.0466 | 0.0477 | 94
0.1052 | 105 | 0.0465 | 0.0476 | 94
0.1052 | 105 | 0.0465 | 0.0475 | 94
0.1052 | 105 | 0.0465 | 0.0478 | 94
0.1052 | 105 | 0.0466 | 0.0476 | 94
0.1052 | 105 | 0.0465 | 0.0477 | 94
0.1052 | 105 | 0.0464 | 0.0476 | 94
0.1052 | 105 | 0.0464 | 0.0477 | 94
0.1052 | 105 | 0.0467 | 0.0474 | 94
0.1052 | 105 | 0.0466 | 0.0477 | 94
0.1052 | 105 | 0.0466 | 0.0477 | 94
0.1052 | 105 | 0.0465 | 0.0475 | 94
0.1052 | 105 | 0.0467 | 0.0477 | 94
0.1052 | 105 | 0.0467 | 0.0476 | 94
0.1052 | 105 | 0.0467 | 0.0477 | 94
0.1052 | 105 | 0.0465 | 0.0475 | 94
0.1052 | 105 | 0.0467 | 0.0476 | 94
0.1052 | 105 | 0.0466 | 0.0477 | 94
0.1052 | 105 | 0.0467 | 0.0474 | 94
0.1052 | 105 | 0.0468 | 0.0475 | 94
0.1052 | 105 | 0.0467 | 0.0476 | 94
0.1052 | 105 | 0.0466 | 0.0475 | 94
0.1052 | 105 | 0.0466 | 0.0478 | 94
0.1051 | 105 | 0.0466 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0467 | 0.0476 | 94
0.1051 | 105 | 0.0468 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0477 | 94
0.1051 | 105 | 0.0466 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0467 | 0.0477 | 94
0.1051 | 105 | 0.0467 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0466 | 0.0478 | 94
0.1051 | 105 | 0.0464 | 0.0477 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0467 | 0.0476 | 94
0.1051 | 105 | 0.0465 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0467 | 0.0475 | 94
0.1051 | 105 | 0.0467 | 0.0476 | 94
0.1051 | 105 | 0.0466 | 0.0474 | 94
0.1051 | 105 | 0.0465 | 0.0475 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0465 | 0.0473 | 94
0.1051 | 105 | 0.0463 | 0.0473 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0464 | 0.0475 | 94
0.1051 | 105 | 0.0465 | 0.0473 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0464 | 0.0475 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0464 | 0.0473 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0463 | 0.0474 | 94
0.1051 | 105 | 0.0464 | 0.0473 | 94
0.1051 | 105 | 0.0464 | 0.0475 | 94
0.1051 | 105 | 0.0465 | 0.0472 | 94
0.1051 | 105 | 0.0464 | 0.0474 | 94
0.1051 | 105 | 0.0464 | 0.0474 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0465 | 0.0473 | 94
0.1051 | 105 | 0.0464 | 0.0474 | 94
0.1051 | 105 | 0.0463 | 0.0475 | 94
0.1051 | 105 | 0.0463 | 0.0473 | 94
0.1051 | 105 | 0.0462 | 0.0474 | 94
0.1051 | 105 | 0.0463 | 0.0472 | 94
0.1051 | 105 | 0.0465 | 0.0473 | 94
0.1051 | 105 | 0.0464 | 0.0474 | 94
0.1051 | 105 | 0.0464 | 0.0473 | 94
0.1051 | 105 | 0.0465 | 0.0475 | 94
0.1051 | 105 | 0.0466 | 0.0475 | 94
0.1051 | 105 | 0.0465 | 0.0474 | 94
0.1051 | 105 | 0.0465 | 0.0471 | 94
0.1051 | 105 | 0.0463 | 0.0472 | 94
0.1051 | 105 | 0.0462 | 0.0474 | 94
0.1051 | 105 | 0.0463 | 0.0473 | 94
0.1051 | 105 | 0.0464 | 0.0472 | 94
0.1051 | 105 | 0.0464 | 0.0472 | 94
0.1051 | 105 | 0.0463 | 0.0473 | 94
0.1051 | 105 | 0.0463 | 0.0472 | 94
0.1051 | 105 | 0.0463 | 0.0472 | 94
0.1051 | 105 | 0.0464 | 0.0472 | 94
0.105 | 105 | 0.0465 | 0.0473 | 94
0.105 | 105 | 0.0463 | 0.0474 | 94
0.105 | 105 | 0.0462 | 0.0473 | 94
0.105 | 105 | 0.0463 | 0.0472 | 94
0.105 | 105 | 0.0463 | 0.0472 | 94
0.105 | 105 | 0.0463 | 0.0472 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0464 | 0.0474 | 94
0.105 | 105 | 0.0464 | 0.0472 | 94
0.105 | 105 | 0.0464 | 0.0471 | 94
0.105 | 105 | 0.0463 | 0.0472 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0463 | 0.0474 | 94
0.105 | 105 | 0.0467 | 0.0477 | 94
0.105 | 105 | 0.0468 | 0.0476 | 94
0.105 | 105 | 0.0467 | 0.0476 | 94
0.105 | 105 | 0.0468 | 0.0476 | 94
0.105 | 105 | 0.0467 | 0.0475 | 94
0.105 | 105 | 0.0467 | 0.0477 | 94
0.105 | 105 | 0.0466 | 0.0475 | 94
0.105 | 105 | 0.0467 | 0.0476 | 94
0.105 | 105 | 0.0467 | 0.0476 | 94
0.105 | 105 | 0.0464 | 0.0473 | 94
0.105 | 105 | 0.0465 | 0.0476 | 94
0.105 | 105 | 0.0465 | 0.0474 | 94
0.105 | 105 | 0.0466 | 0.0477 | 94
0.105 | 105 | 0.0466 | 0.0477 | 94
0.105 | 105 | 0.0467 | 0.0477 | 94
0.105 | 105 | 0.0466 | 0.0477 | 94
0.105 | 105 | 0.0467 | 0.0476 | 94
0.105 | 105 | 0.0466 | 0.0478 | 94
0.105 | 105 | 0.0467 | 0.0475 | 94
0.105 | 105 | 0.0463 | 0.0474 | 94
0.105 | 105 | 0.0465 | 0.0475 | 94
0.105 | 105 | 0.0466 | 0.0477 | 94
0.105 | 105 | 0.0466 | 0.0476 | 94
0.105 | 105 | 0.0464 | 0.0475 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0465 | 0.0474 | 94
0.105 | 105 | 0.0464 | 0.0476 | 94
0.105 | 105 | 0.0464 | 0.0473 | 94
0.105 | 105 | 0.0465 | 0.0475 | 94
0.105 | 105 | 0.0464 | 0.0474 | 94
0.105 | 105 | 0.0465 | 0.0473 | 94
0.105 | 105 | 0.0464 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0474 | 94
0.105 | 105 | 0.0464 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0474 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0464 | 0.0472 | 94
0.105 | 105 | 0.0462 | 0.0473 | 94
0.105 | 105 | 0.0464 | 0.0473 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0464 | 0.0473 | 94
0.105 | 105 | 0.0466 | 0.0474 | 94
0.105 | 105 | 0.0461 | 0.0474 | 94
0.105 | 105 | 0.0462 | 0.0474 | 94
0.105 | 105 | 0.0463 | 0.0472 | 94
0.105 | 105 | 0.0465 | 0.0472 | 94
0.105 | 105 | 0.0464 | 0.0472 | 94
0.105 | 105 | 0.0465 | 0.0474 | 94
0.105 | 105 | 0.0464 | 0.0472 | 94
0.105 | 105 | 0.0462 | 0.0473 | 94
0.105 | 105 | 0.0463 | 0.0472 | 94
0.105 | 105 | 0.0462 | 0.0474 | 94
0.105 | 105 | 0.0463 | 0.0473 | 94
0.105 | 105 | 0.0464 | 0.0472 | 94
0.105 | 105 | 0.0466 | 0.0475 | 94
0.105 | 105 | 0.0467 | 0.0477 | 94
0.105 | 105 | 0.0466 | 0.0478 | 94
0.105 | 105 | 0.0463 | 0.0475 | 94
0.105 | 105 | 0.0466 | 0.0476 | 94
0.105 | 105 | 0.0466 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0475 | 94
0.105 | 105 | 0.0466 | 0.0477 | 94
0.105 | 105 | 0.0464 | 0.0476 | 94
0.105 | 105 | 0.0466 | 0.0476 | 94
0.105 | 105 | 0.0467 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0476 | 94
0.105 | 105 | 0.0466 | 0.0476 | 94
0.105 | 105 | 0.0467 | 0.0477 | 94
0.105 | 105 | 0.0465 | 0.0476 | 94
0.105 | 105 | 0.0466 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0476 | 94
0.105 | 105 | 0.0467 | 0.0477 | 94
0.105 | 105 | 0.0467 | 0.0476 | 94
0.105 | 105 | 0.0465 | 0.0474 | 94
0.105 | 105 | 0.0466 | 0.0475 | 94
0.105 | 105 | 0.0465 | 0.0475 | 94
0.105 | 105 | 0.0466 | 0.0476 | 94
0.105 | 105 | 0.0465 | 0.0477 | 94
0.105 | 105 | 0.0466 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0476 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0465 | 0.0474 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0467 | 0.0476 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0465 | 0.0476 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0477 | 94
0.1049 | 105 | 0.0466 | 0.0477 | 94
0.1049 | 105 | 0.0465 | 0.0474 | 94
0.1049 | 105 | 0.0466 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0474 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0466 | 0.0474 | 94
0.1049 | 105 | 0.0465 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0473 | 94
0.1049 | 105 | 0.0464 | 0.0472 | 94
0.1049 | 105 | 0.0465 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0474 | 94
0.1049 | 105 | 0.0462 | 0.0473 | 94
0.1049 | 105 | 0.0464 | 0.0476 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0463 | 0.0475 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0473 | 94
0.1049 | 105 | 0.0465 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0473 | 94
0.1049 | 105 | 0.0463 | 0.0474 | 94
0.1049 | 105 | 0.0463 | 0.0472 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0473 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0463 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0462 | 0.0475 | 94
0.1049 | 105 | 0.0463 | 0.0474 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0463 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0474 | 94
0.1049 | 105 | 0.0465 | 0.0473 | 94
0.1049 | 105 | 0.0464 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0467 | 0.0476 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0464 | 0.0472 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0463 | 0.0472 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0463 | 0.0472 | 94
0.1049 | 105 | 0.0463 | 0.0473 | 94
0.1049 | 105 | 0.0464 | 0.0472 | 94
0.1049 | 105 | 0.0463 | 0.0472 | 94
0.1049 | 105 | 0.0463 | 0.0472 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0474 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0468 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0468 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0477 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0466 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0465 | 0.0475 | 94
0.1049 | 105 | 0.0467 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0478 | 94
0.1049 | 105 | 0.0468 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0475 | 94
0.1049 | 105 | 0.0467 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0471 | 94
0.1049 | 105 | 0.0464 | 0.0474 | 94
0.1049 | 105 | 0.0464 | 0.0475 | 94
0.1049 | 105 | 0.0462 | 0.0475 | 94
0.1049 | 105 | 0.0464 | 0.0474 | 94
0.1049 | 105 | 0.0467 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0475 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0475 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1049 | 105 | 0.0466 | 0.0477 | 94
0.1049 | 105 | 0.0465 | 0.0476 | 94
0.1049 | 105 | 0.0465 | 0.0476 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0467 | 0.0477 | 94
0.1049 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0466 | 0.0477 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0467 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0464 | 0.0474 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0463 | 0.0474 | 94
0.1048 | 105 | 0.0466 | 0.0475 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0467 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0475 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0466 | 0.0477 | 94
0.1048 | 105 | 0.0464 | 0.0474 | 94
0.1048 | 105 | 0.0465 | 0.0473 | 94
0.1048 | 105 | 0.0468 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0467 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0464 | 0.0473 | 94
0.1048 | 105 | 0.0464 | 0.0474 | 94
0.1048 | 105 | 0.0464 | 0.0474 | 94
0.1048 | 105 | 0.0464 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0473 | 94
0.1048 | 105 | 0.0466 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0466 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0462 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0464 | 0.0472 | 94
0.1048 | 105 | 0.0466 | 0.0475 | 94
0.1048 | 105 | 0.0463 | 0.0474 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0467 | 0.0476 | 94
0.1048 | 105 | 0.0467 | 0.0477 | 94
0.1048 | 105 | 0.0465 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0477 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0464 | 0.0474 | 94
0.1048 | 105 | 0.0465 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0475 | 94
0.1048 | 105 | 0.0465 | 0.0474 | 94
0.1048 | 105 | 0.0466 | 0.0477 | 94
0.1048 | 105 | 0.0464 | 0.0473 | 94
0.1048 | 105 | 0.0463 | 0.0474 | 94
0.1048 | 105 | 0.0464 | 0.0474 | 94
0.1048 | 105 | 0.0464 | 0.0473 | 94
0.1048 | 105 | 0.0466 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0476 | 94
0.1048 | 105 | 0.0465 | 0.0476 | 94
0.1048 | 105 | 0.0466 | 0.0474 | 94
0.1048 | 105 | 0.0463 | 0.0473 | 94
0.1048 | 105 | 0.0463 | 0.0473 | 94
0.1047 | 105 | 0.0465 | 0.0477 | 94
0.1047 | 105 | 0.0466 | 0.0476 | 94
0.1047 | 105 | 0.0465 | 0.0474 | 94
0.1047 | 105 | 0.0466 | 0.0476 | 94
0.1047 | 105 | 0.0465 | 0.0475 | 94
0.1047 | 105 | 0.0464 | 0.0474 | 94
0.1047 | 105 | 0.0463 | 0.0474 | 94
0.1047 | 105 | 0.0462 | 0.0473 | 94
0.1047 | 105 | 0.0466 | 0.0474 | 94
0.1047 | 105 | 0.0463 | 0.0472 | 94
0.1047 | 105 | 0.0465 | 0.0473 | 94
0.1047 | 105 | 0.0466 | 0.0474 | 94
0.1047 | 105 | 0.0466 | 0.0475 | 94
0.1047 | 105 | 0.0464 | 0.0472 | 94
0.1047 | 105 | 0.0466 | 0.0474 | 94
0.1047 | 105 | 0.0467 | 0.0475 | 94
0.1047 | 105 | 0.0465 | 0.0474 | 94
0.1047 | 105 | 0.0465 | 0.0475 | 94
0.1047 | 105 | 0.0464 | 0.0475 | 94
0.1047 | 105 | 0.0465 | 0.0473 | 94
0.1047 | 105 | 0.0466 | 0.0475 | 94
0.1047 | 105 | 0.0463 | 0.0474 | 94
0.1047 | 105 | 0.0463 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0463 | 0.047 | 93
0.1047 | 105 | 0.0463 | 0.047 | 93
0.1047 | 105 | 0.0463 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0461 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0463 | 0.047 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0461 | 0.047 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0461 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0471 | 93
0.1047 | 105 | 0.0459 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0463 | 0.0471 | 93
0.1047 | 105 | 0.0461 | 0.0471 | 93
0.1047 | 105 | 0.0463 | 0.0471 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.046 | 0.0473 | 93
0.1047 | 105 | 0.0461 | 0.0472 | 93
0.1047 | 105 | 0.0462 | 0.0472 | 93
0.1047 | 105 | 0.0461 | 0.047 | 93
0.1047 | 105 | 0.0459 | 0.0469 | 93
0.1047 | 105 | 0.0458 | 0.0467 | 93
0.1047 | 105 | 0.0456 | 0.0464 | 92
0.1047 | 105 | 0.0456 | 0.0465 | 92
0.1047 | 105 | 0.0458 | 0.0465 | 92
0.1047 | 105 | 0.0457 | 0.0466 | 92
0.1047 | 105 | 0.0457 | 0.0466 | 92
0.1047 | 105 | 0.0457 | 0.0466 | 92
0.1047 | 105 | 0.0457 | 0.0467 | 92
0.1047 | 105 | 0.0456 | 0.0465 | 92
0.1047 | 105 | 0.0457 | 0.0466 | 92
0.1047 | 105 | 0.0457 | 0.0464 | 92
0.1047 | 105 | 0.0457 | 0.0466 | 92
0.1047 | 105 | 0.0457 | 0.0464 | 92
0.1047 | 105 | 0.0456 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0466 | 92
0.1047 | 105 | 0.0456 | 0.0465 | 92
0.1047 | 105 | 0.0456 | 0.0466 | 92
0.1047 | 105 | 0.0455 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0466 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0455 | 0.0464 | 92
0.1047 | 105 | 0.0456 | 0.0466 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0454 | 0.0465 | 92
0.1047 | 105 | 0.0456 | 0.0463 | 92
0.1047 | 105 | 0.0456 | 0.0465 | 92
0.1047 | 105 | 0.0456 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0455 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0455 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0463 | 92
0.1047 | 105 | 0.0455 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0454 | 0.0464 | 92
0.1047 | 105 | 0.0457 | 0.0464 | 92
0.1047 | 105 | 0.0454 | 0.0464 | 92
0.1047 | 105 | 0.0456 | 0.0465 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0456 | 0.0464 | 92
0.1047 | 105 | 0.0455 | 0.0465 | 92
0.1047 | 105 | 0.0454 | 0.0465 | 92
0.1047 | 105 | 0.0454 | 0.0463 | 92
0.1047 | 105 | 0.0453 | 0.0462 | 92
0.1047 | 105 | 0.0454 | 0.0463 | 92
0.1047 | 105 | 0.0455 | 0.0463 | 92
0.1047 | 105 | 0.0455 | 0.0463 | 92
0.1046 | 105 | 0.0455 | 0.0464 | 92
0.1046 | 105 | 0.0451 | 0.0456 | 91
0.1046 | 105 | 0.0452 | 0.0459 | 91
0.1046 | 105 | 0.0448 | 0.0457 | 91
0.1046 | 105 | 0.045 | 0.0459 | 91
0.1046 | 105 | 0.0449 | 0.0459 | 91
0.1046 | 105 | 0.045 | 0.046 | 91
0.1046 | 105 | 0.045 | 0.0459 | 91
0.1046 | 105 | 0.0452 | 0.046 | 91
0.1046 | 105 | 0.0451 | 0.046 | 91
0.1046 | 105 | 0.045 | 0.0459 | 91
0.1046 | 105 | 0.0449 | 0.0458 | 91
0.1046 | 105 | 0.0451 | 0.0461 | 91
0.1046 | 105 | 0.0449 | 0.046 | 91
0.1046 | 105 | 0.0451 | 0.0459 | 91
0.1046 | 105 | 0.0444 | 0.0453 | 90
0.1046 | 105 | 0.0441 | 0.045 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.044 | 0.0449 | 89
0.1046 | 105 | 0.0438 | 0.0447 | 89
0.1046 | 105 | 0.0438 | 0.0447 | 89
0.1046 | 105 | 0.044 | 0.0448 | 89
0.1046 | 105 | 0.0436 | 0.0446 | 88
0.1046 | 105 | 0.0435 | 0.0444 | 88
0.1046 | 105 | 0.0436 | 0.0444 | 88
0.1046 | 105 | 0.0437 | 0.0445 | 88
0.1046 | 105 | 0.0437 | 0.0446 | 88
0.1046 | 105 | 0.0434 | 0.0444 | 88
0.1046 | 105 | 0.0427 | 0.0436 | 86
0.1046 | 105 | 0.0428 | 0.0435 | 86
0.1046 | 105 | 0.0422 | 0.0431 | 85
0.1046 | 105 | 0.0419 | 0.0427 | 85
0.1046 | 105 | 0.0418 | 0.0428 | 85
0.1046 | 105 | 0.0415 | 0.0424 | 84
0.1046 | 105 | 0.0413 | 0.0423 | 84
0.1046 | 105 | 0.0415 | 0.0423 | 84
0.1046 | 105 | 0.0416 | 0.0423 | 84
0.1046 | 105 | 0.0416 | 0.0427 | 84
0.1046 | 105 | 0.0417 | 0.0427 | 84
0.1046 | 105 | 0.0408 | 0.0419 | 83
0.1046 | 105 | 0.041 | 0.0416 | 83
0.1046 | 105 | 0.0403 | 0.0412 | 82
0.1046 | 105 | 0.0406 | 0.0415 | 82
0.1046 | 105 | 0.0407 | 0.0415 | 82
0.1046 | 105 | 0.0404 | 0.0412 | 82
0.1046 | 105 | 0.0403 | 0.0411 | 81
0.1046 | 105 | 0.0402 | 0.0411 | 81
0.1046 | 105 | 0.0401 | 0.0412 | 81
0.1046 | 105 | 0.0401 | 0.0409 | 81
0.1046 | 105 | 0.0402 | 0.0411 | 81
0.1046 | 105 | 0.0403 | 0.0411 | 81
0.1046 | 105 | 0.0399 | 0.0405 | 80
0.1046 | 105 | 0.0392 | 0.04 | 79
0.1046 | 105 | 0.039 | 0.0398 | 79
0.1046 | 105 | 0.0389 | 0.0396 | 79
0.1046 | 105 | 0.0388 | 0.0398 | 79
0.1046 | 105 | 0.0388 | 0.0398 | 79
0.1046 | 105 | 0.0387 | 0.0398 | 79
0.1046 | 105 | 0.0388 | 0.0397 | 79
0.1046 | 105 | 0.0389 | 0.0396 | 79
0.1046 | 105 | 0.0388 | 0.0397 | 79
0.1046 | 105 | 0.0389 | 0.0396 | 79
0.1046 | 105 | 0.0386 | 0.0394 | 78
0.1046 | 105 | 0.0387 | 0.0396 | 78
0.1046 | 105 | 0.0387 | 0.0397 | 78
0.1046 | 105 | 0.0385 | 0.0396 | 78
0.1046 | 105 | 0.0388 | 0.0396 | 78
0.1046 | 105 | 0.0387 | 0.0397 | 78
0.1046 | 105 | 0.0387 | 0.0395 | 78
0.1046 | 105 | 0.0387 | 0.0395 | 78
0.1046 | 105 | 0.038 | 0.0385 | 77
0.1046 | 105 | 0.038 | 0.0386 | 77
0.1046 | 105 | 0.0379 | 0.0386 | 77
0.1046 | 105 | 0.0375 | 0.038 | 76
0.1046 | 105 | 0.0373 | 0.0379 | 75
0.1046 | 105 | 0.0371 | 0.0378 | 75
0.1046 | 105 | 0.037 | 0.0377 | 75
0.1046 | 105 | 0.0369 | 0.0377 | 75
0.1045 | 105 | 0.0363 | 0.0373 | 74
0.1045 | 105 | 0.0361 | 0.0367 | 73
0.1045 | 105 | 0.0363 | 0.0371 | 73
0.1045 | 105 | 0.0355 | 0.0364 | 72
0.1045 | 105 | 0.0344 | 0.0352 | 70
0.1045 | 105 | 0.0346 | 0.0353 | 70
0.1045 | 105 | 0.0344 | 0.0348 | 69
0.1045 | 105 | 0.0344 | 0.035 | 69
0.1045 | 105 | 0.0336 | 0.034 | 68
0.1045 | 105 | 0.033 | 0.0336 | 67
0.1045 | 105 | 0.0325 | 0.0331 | 66
0.1045 | 105 | 0.0329 | 0.0335 | 66
0.1045 | 105 | 0.0321 | 0.033 | 65
0.1045 | 105 | 0.0306 | 0.0311 | 62
0.1045 | 105 | 0.0304 | 0.0312 | 62
0.1045 | 105 | 0.0304 | 0.0311 | 62
0.1045 | 105 | 0.0305 | 0.031 | 62
0.1045 | 105 | 0.0304 | 0.0311 | 62
0.1045 | 105 | 0.0301 | 0.0308 | 61
0.1045 | 105 | 0.0303 | 0.0307 | 61
0.1045 | 105 | 0.0303 | 0.0308 | 61
0.1045 | 105 | 0.0301 | 0.0307 | 61
0.1045 | 105 | 0.0302 | 0.0306 | 61
0.1045 | 105 | 0.0301 | 0.0305 | 61
0.1045 | 105 | 0.0303 | 0.0306 | 61
0.1045 | 105 | 0.03 | 0.0306 | 61
0.1045 | 105 | 0.0304 | 0.0306 | 61
0.1045 | 105 | 0.0301 | 0.0307 | 61
0.1045 | 105 | 0.0303 | 0.0309 | 61
0.1045 | 105 | 0.0302 | 0.0308 | 61
0.1045 | 105 | 0.0296 | 0.0301 | 60
0.1045 | 105 | 0.0299 | 0.0304 | 60
0.1045 | 105 | 0.0293 | 0.0297 | 59
0.1045 | 105 | 0.0278 | 0.028 | 56
0.1045 | 105 | 0.0276 | 0.028 | 56
0.1045 | 105 | 0.0269 | 0.0272 | 54
0.1045 | 105 | 0.0265 | 0.027 | 54
0.1045 | 105 | 0.0265 | 0.0271 | 54
0.1045 | 105 | 0.0266 | 0.0269 | 54
0.1045 | 105 | 0.0265 | 0.027 | 54
0.1045 | 105 | 0.0262 | 0.0267 | 53
0.1045 | 105 | 0.0265 | 0.0269 | 53
0.1045 | 105 | 0.0258 | 0.0265 | 52
0.1045 | 105 | 0.0256 | 0.0259 | 52
0.1045 | 105 | 0.0254 | 0.0261 | 52
0.1045 | 105 | 0.0255 | 0.026 | 52
0.1045 | 105 | 0.0256 | 0.026 | 52
0.1045 | 105 | 0.0255 | 0.026 | 52
0.1045 | 105 | 0.0258 | 0.0264 | 52
0.1045 | 105 | 0.0254 | 0.026 | 51
0.1045 | 105 | 0.0251 | 0.0258 | 51
0.1045 | 105 | 0.025 | 0.0256 | 51
0.1045 | 105 | 0.024 | 0.0246 | 49
0.1045 | 105 | 0.0244 | 0.025 | 49
0.1045 | 105 | 0.0245 | 0.0248 | 49
0.1045 | 105 | 0.0239 | 0.0242 | 48
0.1045 | 105 | 0.0238 | 0.0243 | 48
0.1045 | 105 | 0.0235 | 0.0237 | 47
0.1045 | 105 | 0.0232 | 0.0234 | 47
0.1045 | 105 | 0.0229 | 0.0231 | 46
0.1045 | 105 | 0.0224 | 0.0228 | 45
0.1045 | 105 | 0.0217 | 0.0218 | 44
0.1045 | 105 | 0.0212 | 0.0216 | 43
0.1045 | 105 | 0.0215 | 0.0218 | 43
0.1045 | 105 | 0.0203 | 0.0206 | 41
0.1045 | 105 | 0.0197 | 0.0201 | 40
0.1045 | 105 | 0.0192 | 0.0195 | 39
0.1045 | 105 | 0.0187 | 0.0191 | 38
0.1045 | 105 | 0.0186 | 0.0189 | 38
0.1045 | 105 | 0.0189 | 0.0193 | 38
0.1045 | 105 | 0.0186 | 0.0189 | 38
0.1045 | 105 | 0.0188 | 0.0189 | 38
0.1045 | 105 | 0.0186 | 0.0189 | 38
0.1045 | 105 | 0.0186 | 0.0189 | 38
0.1045 | 105 | 0.0185 | 0.0186 | 37
0.1045 | 105 | 0.0185 | 0.0187 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0185 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0182 | 0.019 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0187 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0185 | 0.0187 | 37
0.1045 | 105 | 0.0183 | 0.0183 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0185 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0185 | 37
0.1045 | 105 | 0.0185 | 0.0187 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0182 | 0.0185 | 37
0.1045 | 105 | 0.0183 | 0.0185 | 37
0.1045 | 105 | 0.0183 | 0.0184 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0184 | 37
0.1045 | 105 | 0.0183 | 0.0184 | 37
0.1045 | 105 | 0.0184 | 0.0187 | 37
0.1045 | 105 | 0.0185 | 0.0188 | 37
0.1045 | 105 | 0.0183 | 0.0188 | 37
0.1045 | 105 | 0.0185 | 0.0187 | 37
0.1045 | 105 | 0.0185 | 0.0187 | 37
0.1045 | 105 | 0.0184 | 0.0186 | 37
0.1045 | 105 | 0.0184 | 0.0188 | 37
0.1045 | 105 | 0.0182 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0186 | 37
0.1045 | 105 | 0.0183 | 0.0187 | 37
0.1044 | 104 | 0.0185 | 0.0187 | 37
0.1044 | 104 | 0.0184 | 0.0185 | 37
0.1044 | 104 | 0.0184 | 0.0186 | 37
0.1044 | 104 | 0.0183 | 0.0186 | 37
0.1044 | 104 | 0.0185 | 0.0189 | 37
0.1044 | 104 | 0.0186 | 0.0188 | 37
0.1044 | 104 | 0.0186 | 0.0188 | 37
0.1044 | 104 | 0.0187 | 0.0187 | 37
0.1044 | 104 | 0.0186 | 0.0188 | 37
0.1044 | 104 | 0.0185 | 0.0188 | 37
0.1044 | 104 | 0.0185 | 0.0188 | 37
0.1044 | 104 | 0.0186 | 0.0188 | 37
0.1044 | 104 | 0.0185 | 0.0188 | 37
0.1044 | 104 | 0.0185 | 0.0188 | 37
0.1044 | 104 | 0.0185 | 0.0187 | 37
0.1044 | 104 | 0.0185 | 0.0186 | 37
0.1044 | 104 | 0.0185 | 0.0187 | 37
0.1044 | 104 | 0.0182 | 0.0185 | 37
0.1044 | 104 | 0.0186 | 0.0188 | 37
0.1044 | 104 | 0.0176 | 0.0175 | 35
0.1044 | 104 | 0.0174 | 0.0171 | 35
0.1044 | 104 | 0.0173 | 0.0177 | 35
0.1044 | 104 | 0.0172 | 0.0175 | 35
0.1044 | 104 | 0.0161 | 0.0161 | 32
0.1044 | 104 | 0.0156 | 0.0159 | 32
0.1044 | 104 | 0.0161 | 0.0162 | 32
0.1044 | 104 | 0.0156 | 0.0155 | 31
0.1044 | 104 | 0.0146 | 0.0146 | 29
0.1044 | 104 | 0.0118 | 0.0119 | 24
0.1044 | 104 | 0.0118 | 0.0119 | 24
0.1044 | 104 | 0.0113 | 0.0114 | 23
0.1044 | 104 | 0.0109 | 0.0111 | 22
0.1044 | 104 | 0.0109 | 0.0111 | 22
0.1044 | 104 | 0.0109 | 0.0111 | 22
0.1044 | 104 | 0.0109 | 0.0111 | 22
0.1044 | 104 | 0.0098 | 0.0097 | 20
0.1044 | 104 | 0.0097 | 0.0098 | 20
0.1044 | 104 | 0.0099 | 0.01 | 20
0.1044 | 104 | 0.0102 | 0.0102 | 20
0.1044 | 104 | 0.0095 | 0.0095 | 19
0.1044 | 104 | 0.0082 | 0.0083 | 17
0.1044 | 104 | 0.0083 | 0.0084 | 17
0.1044 | 104 | 0.0083 | 0.0083 | 17
0.1044 | 104 | 0.0082 | 0.0085 | 17
0.1044 | 104 | 0.0085 | 0.0086 | 17
0.1044 | 104 | 0.0084 | 0.0082 | 17
0.1044 | 104 | 0.0083 | 0.0085 | 17
0.1044 | 104 | 0.0082 | 0.0084 | 17
0.1044 | 104 | 0.0085 | 0.0083 | 17
0.1044 | 104 | 0.0082 | 0.0082 | 16
0.1044 | 104 | 0.0082 | 0.0081 | 16
0.1044 | 104 | 0.0081 | 0.0082 | 16
0.1044 | 104 | 0.0077 | 0.0078 | 16
0.1044 | 104 | 0.0081 | 0.0083 | 16
0.1044 | 104 | 0.0082 | 0.0082 | 16
0.1044 | 104 | 0.0069 | 0.0066 | 14
0.1044 | 104 | 0.0062 | 0.0064 | 13
0.1044 | 104 | 0.005 | 0.0049 | 10
0.1044 | 104 | 0.0049 | 0.0049 | 10
0.1044 | 104 | 0.003 | 0.0055 | 9
0.1044 | 104 | 0.0035 | 0.0057 | 9
0.1044 | 104 | 0.0032 | 0.0045 | 8
0.1044 | 104 | 0.0019 | 0.0059 | 8
0.1044 | 104 | 0.003 | 0.0053 | 8
0.1044 | 104 | 0.0036 | 0.0034 | 7
0.1044 | 104 | 0.0035 | 0.0037 | 7
0.1044 | 104 | 0.0015 | 0.0059 | 7
0.1044 | 104 | 0.0017 | 0.0055 | 7
0.1044 | 104 | 0.0018 | 0.0056 | 7
0.1044 | 104 | 0.0036 | 0.0033 | 7
0.1044 | 104 | 0.0037 | 0.0036 | 7
0.1044 | 104 | 0.002 | 0.0044 | 6
0.1044 | 104 | 0.003 | 0.0034 | 6
0.1044 | 104 | 0.0025 | 0.0032 | 6
0.1044 | 104 | 0.0024 | 0.0032 | 6
0.1044 | 104 | 0.0026 | 0.0032 | 6
0.1044 | 104 | 0.0023 | 0.0032 | 6
0.1044 | 104 | 0.0026 | 0.0031 | 6
0.1044 | 104 | 0.0025 | 0.0032 | 6
0.1044 | 104 | 0.0026 | 0.0032 | 6
0.1044 | 104 | 0.0029 | 0.0032 | 6
0.1044 | 104 | 0.0003 | 0.0061 | 6
0.1044 | 104 | 0.0006 | 0.0058 | 6
0.1044 | 104 | 0.0022 | 0.0034 | 6
0.1044 | 104 | 0.0002 | 0.0058 | 6
0.1044 | 104 | 0.0029 | 0.0029 | 6
0.1044 | 104 | 0.0031 | 0.0028 | 6
0.1044 | 104 | 0.0023 | 0.0024 | 5
0.1044 | 104 | 0.0024 | 0.0027 | 5
0.1044 | 104 | 0.0021 | 0.0033 | 5
0.1044 | 104 | 0.0022 | 0.003 | 5
0.1044 | 104 | 0.0021 | 0.0031 | 5
0.1044 | 104 | 0.002 | 0.0029 | 5
0.1044 | 104 | 0.0021 | 0.0029 | 5
0.1044 | 104 | 0.0022 | 0.0027 | 5
0.1044 | 104 | 0.0024 | 0.0029 | 5
0.1044 | 104 | 0.0023 | 0.0031 | 5
0.1044 | 104 | 0.0022 | 0.0031 | 5
0.1044 | 104 | 0.0023 | 0.0029 | 5
0.1044 | 104 | 0.0025 | 0.0029 | 5
0.1044 | 104 | 0 | 0.0047 | 5
0.1044 | 104 | 0.0017 | 0.003 | 5
0.1044 | 104 | 0.0022 | 0.0032 | 5
0.1044 | 104 | 0.0016 | 0.0034 | 5
0.1044 | 104 | 0.0017 | 0.0032 | 5
0.1044 | 104 | 0.0003 | 0.0051 | 5
0.1044 | 104 | 0.0015 | 0.0026 | 4
0.1044 | 104 | 0.0019 | 0.0025 | 4
0.1044 | 104 | 0.0017 | 0.0024 | 4
0.1044 | 104 | 0.0015 | 0.002 | 4
0.1044 | 104 | 0.0017 | 0.0023 | 4
0.1044 | 104 | 0.0013 | 0.0022 | 4
0.1044 | 104 | 0 | 0.0037 | 4
0.1044 | 104 | 0 | 0.0038 | 4
0.1044 | 104 | 0.0001 | 0.0037 | 4
0.1044 | 104 | 0 | 0.0035 | 4
0.1044 | 104 | 0.0003 | 0.0035 | 4
0.1044 | 104 | 0 | 0.0043 | 4
0.1044 | 104 | 0.0014 | 0.0012 | 3
0.1043 | 104 | 0.0015 | 0.0018 | 3
0.1043 | 104 | 0.0012 | 0.0013 | 3
0.1043 | 104 | 0.0011 | 0.0015 | 3
0.1043 | 104 | 0.0015 | 0.0018 | 3
0.1043 | 104 | 0 | 0.0032 | 3
0.1043 | 104 | 0.0007 | 0.0026 | 3
0.1043 | 104 | 0 | 0.0028 | 3
0.1043 | 104 | 0.001 | 0.0007 | 2
0.1043 | 104 | 0.0008 | 0.0013 | 2
0.1043 | 104 | 0.0009 | 0.0015 | 2
0.1043 | 104 | 0.001 | 0.001 | 2
0.1043 | 104 | 0.0009 | 0.0013 | 2
0.1043 | 104 | 0.0007 | 0.0014 | 2
0.1043 | 104 | 0.0009 | 0.0014 | 2
0.1043 | 104 | 0 | 0.0024 | 2
0.1043 | 104 | 0.0001 | 0.0018 | 2
0.1043 | 104 | 0.0001 | 0.0017 | 2
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1043 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1042 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.1041 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.104 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1039 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1038 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1037 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1036 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1035 | 104
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1034 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1033 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1032 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.1031 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.103 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1029 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1028 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1027 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1026 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1025 | 103
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1024 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1023 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1022 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.1021 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.102 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1019 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1018 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1017 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1016 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1015 | 102
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1014 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1013 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1012 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.1011 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.101 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1009 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1008 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1007 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1006 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1005 | 101
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1004 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1003 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1002 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1001 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.1 | 100
0.0999 | 100
0.0999 | 100
0.0997 | 100
0.0996 | 100
0.0996 | 100
0.0995 | 100
0.0995 | 100
0.0995 | 100
0.0995 | 100
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0994 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0993 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0992 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.0991 | 99
0.099 | 99
0.0989 | 99
0.0989 | 99
0.0989 | 99
0.0988 | 99
0.0988 | 99
0.0988 | 99
0.0988 | 99
0.0987 | 99
0.0987 | 99
0.0987 | 99
0.0987 | 99
0.0987 | 99
0.0985 | 99
0.0979 | 98
0.0978 | 98
0.0972 | 97
0.097 | 97
0.097 | 97
0.0969 | 97
0.096 | 96
0.0958 | 96
0.0958 | 96
0.0948 | 95
0.0947 | 95
0.0946 | 95
0.0945 | 95
0.0941 | 94
0.0938 | 94
0.0938 | 94
0.0936 | 94
0.093 | 93
0.0929 | 93
0.0928 | 93
0.0926 | 93
0.0925 | 93
0.0921 | 92
0.0918 | 92
0.0918 | 92
0.0915 | 92
0.0914 | 91
0.0914 | 91
0.0912 | 91
0.0911 | 91
0.0911 | 91
0.091 | 91
0.0909 | 91
0.0908 | 91
0.0908 | 91
0.0906 | 91
0.0905 | 91
0.0905 | 91
0.0905 | 91
0.0904 | 90
0.0903 | 90
0.09 | 90
0.09 | 90
0.0897 | 90
0.0889 | 89
0.0888 | 89
0.0888 | 89
0.0888 | 89
0.0887 | 89
0.0885 | 89
0.0882 | 88
0.0881 | 88
0.0881 | 88
0.0879 | 88
0.0879 | 88
0.0876 | 88
0.0876 | 88
0.0876 | 88
0.0876 | 88
0.0875 | 88
0.0862 | 86
0.0862 | 86
0.0858 | 86
0.0856 | 86
0.0856 | 86
0.0854 | 85
0.0851 | 85
0.085 | 85
0.0849 | 85
0.0845 | 85
0.0842 | 84
0.0839 | 84
0.0837 | 84
0.0835 | 84
0.0832 | 83
0.0826 | 83
0.0826 | 83
0.0826 | 83
0.0825 | 83
0.0825 | 83
0.0825 | 83
0.0821 | 82
0.0812 | 81
0.0812 | 81
0.081 | 81
0.0808 | 81
0.0807 | 81
0.0804 | 80
0.0802 | 80
0.0799 | 80
0.0798 | 80
0.0797 | 80
0.0797 | 80
0.0795 | 80
0.0795 | 80
0.0795 | 80
0.0794 | 79
0.0793 | 79
0.0793 | 79
0.0792 | 79
0.0789 | 79
0.0789 | 79
0.0789 | 79
0.0787 | 79
0.0781 | 78
0.0777 | 78
0.0776 | 78
0.0774 | 77
0.0771 | 77
0.0768 | 77
0.0768 | 77
0.0766 | 77
0.0759 | 76
0.0754 | 75
0.0754 | 75
0.0753 | 75
0.0747 | 75
0.0746 | 75
0.0744 | 74
0.0744 | 74
0.0734 | 73
0.0733 | 73
0.0732 | 73
0.0727 | 73
0.0727 | 73
0.0726 | 73
0.0726 | 73
0.0725 | 73
0.0723 | 72
0.0722 | 72
0.0722 | 72
0.0721 | 72
0.0719 | 72
0.0719 | 72
0.0718 | 72
0.0716 | 72
0.0715 | 72
0.0714 | 71
0.0713 | 71
0.0712 | 71
0.0708 | 71
0.0708 | 71
0.0708 | 71
0.0707 | 71
0.0701 | 70
0.0698 | 70
0.0698 | 70
0.0697 | 70
0.0695 | 70
0.0694 | 69
0.0693 | 69
0.0692 | 69
0.069 | 69
0.0689 | 69
0.0689 | 69
0.0689 | 69
0.0689 | 69
0.0689 | 69
0.0689 | 69
0.0689 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0688 | 69
0.0687 | 69
0.0687 | 69
0.0687 | 69
0.0687 | 69
0.0687 | 69
0.0687 | 69
0.0687 | 69
0.0686 | 69
0.0685 | 69
0.0685 | 69
0.0685 | 69
0.0685 | 69
0.0685 | 69
0.0685 | 69
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0684 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0683 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0682 | 68
0.0681 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.068 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0679 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0678 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0677 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0676 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0675 | 68
0.0674 | 67
0.0674 | 67
0.0674 | 67
0.0674 | 67
0.0674 | 67
0.0674 | 67
0.0674 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0673 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0672 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.0671 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.067 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0669 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0668 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0667 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0666 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0665 | 67
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0664 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0663 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0662 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.0661 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.066 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0659 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0658 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0657 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0656 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0655 | 66
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0654 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0653 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0652 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.0651 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.065 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0649 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0648 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0647 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0646 | 65
0.0645 | 65
0.0645 | 65
0.0645 | 65
0.0643 | 64
0.0635 | 64
0.0635 | 64
0.0633 | 63
0.0633 | 63
0.0631 | 63
0.0629 | 63
0.0625 | 63
0.0621 | 62
0.0615 | 62
0.0614 | 61
0.0613 | 61
0.0609 | 61
0.0609 | 61
0.0609 | 61
0.0607 | 61
0.0605 | 61
0.0605 | 61
0.0604 | 60
0.0603 | 60
0.0601 | 60
0.0601 | 60
0.06 | 60
0.06 | 60
0.0599 | 60
0.0598 | 60
0.0591 | 59
0.059 | 59
0.0588 | 59
0.0587 | 59
0.0587 | 59
0.0587 | 59
0.0585 | 59
0.0585 | 59
0.0582 | 58
0.058 | 58
0.0577 | 58
0.0574 | 57
0.0573 | 57
0.0572 | 57
0.0568 | 57
0.0567 | 57
0.0566 | 57
0.0565 | 57
0.0563 | 56
0.0563 | 56
0.0559 | 56
0.0554 | 55
0.0552 | 55
0.0549 | 55
0.0548 | 55
0.0548 | 55
0.0547 | 55
0.0546 | 55
0.0545 | 55
0.0542 | 54
0.0539 | 54
0.0536 | 54
0.0535 | 54
0.0533 | 53
0.0532 | 53
0.053 | 53
0.053 | 53
0.0528 | 53
0.0524 | 52
0.0523 | 52
0.0523 | 52
0.0519 | 52
0.0518 | 52
0.0516 | 52
0.0515 | 52
0.0514 | 51
0.0514 | 51
0.0513 | 51
0.0512 | 51
0.0512 | 51
0.0511 | 51
0.0511 | 51
0.0505 | 51
0.0501 | 50
0.05 | 50
0.0499 | 50
0.0496 | 50
0.0492 | 49
0.049 | 49
0.0488 | 49
0.0479 | 48
0.0476 | 48
0.0475 | 48
0.0473 | 47
0.0469 | 47
0.0468 | 47
0.0467 | 47
0.0465 | 47
0.0463 | 46
0.0461 | 46
0.046 | 46
0.0456 | 46
0.0456 | 46
0.0455 | 46
0.0455 | 46
0.0453 | 45
0.0452 | 45
0.0452 | 45
0.045 | 45
0.0442 | 44
0.0442 | 44
0.0442 | 44
0.0439 | 44
0.0437 | 44
0.0437 | 44
0.0436 | 44
0.0435 | 44
0.0434 | 43
0.0434 | 43
0.0432 | 43
0.043 | 43
0.043 | 43
0.0428 | 43
0.0428 | 43
0.0428 | 43
0.0424 | 42
0.0424 | 42
0.0422 | 42
0.0421 | 42
0.042 | 42
0.042 | 42
0.042 | 42
0.0419 | 42
0.0419 | 42
0.0418 | 42
0.0418 | 42
0.0417 | 42
0.0416 | 42
0.0416 | 42
0.0416 | 42
0.0416 | 42
0.0416 | 42
0.0416 | 42
0.0416 | 42
0.0415 | 42
0.0415 | 42
0.0414 | 41
0.0413 | 41
0.0413 | 41
0.0413 | 41
0.0413 | 41
0.0412 | 41
0.0412 | 41
0.0411 | 41
0.0411 | 41
0.041 | 41
0.041 | 41
0.041 | 41
0.041 | 41
0.0409 | 41
0.0409 | 41
0.0409 | 41
0.0409 | 41
0.0409 | 41
0.0408 | 41
0.0407 | 41
0.0407 | 41
0.0406 | 41
0.0406 | 41
0.0406 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0405 | 41
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0404 | 40
0.0403 | 40
0.0403 | 40
0.0403 | 40
0.0403 | 40
0.0403 | 40
0.0402 | 40
0.0402 | 40
0.0402 | 40
0.0402 | 40
0.0402 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.0401 | 40
0.04 | 40
0.04 | 40
0.04 | 40
0.0399 | 40
0.0399 | 40
0.0399 | 40
0.0399 | 40
0.0398 | 40
0.0398 | 40
0.0398 | 40
0.0398 | 40
0.0398 | 40
0.0398 | 40
0.0397 | 40
0.0397 | 40
0.0397 | 40
0.0396 | 40
0.0396 | 40
0.0395 | 40
0.0394 | 39
0.0394 | 39
0.0394 | 39
0.0389 | 39
0.0389 | 39
0.0383 | 38
0.0382 | 38
0.0378 | 38
0.0375 | 38
0.0367 | 37
0.0363 | 36
0.0361 | 36
0.0352 | 35
0.0351 | 35
0.0351 | 35
0.0351 | 35
0.0349 | 35
0.0341 | 34
0.0333 | 33
0.0331 | 33
0.0331 | 33
0.033 | 33
0.0328 | 33
0.0326 | 33
0.0323 | 32
0.0322 | 32
0.0321 | 32
0.032 | 32
0.032 | 32
0.0319 | 32
0.0319 | 32
0.0318 | 32
0.0318 | 32
0.0318 | 32
0.0318 | 32
0.0315 | 32
0.0314 | 31
0.0313 | 31
0.0312 | 31
0.0311 | 31
0.0311 | 31
0.0308 | 31
0.0307 | 31
0.0306 | 31
0.0306 | 31
0.0306 | 31
0.0304 | 30
0.0299 | 30
0.0294 | 29
0.0294 | 29
0.0293 | 29
0.0293 | 29
0.0288 | 29
0.0287 | 29
0.0286 | 29
0.0286 | 29
0.0284 | 28
0.0282 | 28
0.0281 | 28
0.028 | 28
0.0279 | 28
0.0279 | 28
0.0274 | 27
0.0271 | 27
0.0271 | 27
0.0269 | 27
0.0264 | 26
0.0258 | 26
0.0254 | 25
0.0245 | 25
0.0233 | 23
0.0232 | 23
0.023 | 23
0.023 | 23
0.0228 | 23
0.0226 | 23
0.0221 | 22
0.0221 | 22
0.0213 | 21
0.0207 | 21
0.0206 | 21
0.0204 | 20
0.0197 | 20
0.0194 | 19
0.0193 | 19
0.0179 | 18
0.0168 | 17
0.0155 | 16
0.0152 | 15
0.0146 | 15
0.0142 | 14
0.0141 | 14
0.014 | 14
0.0139 | 14
0.0138 | 14
0.0134 | 13
0.0128 | 13
0.0123 | 12
0.0122 | 12
0.0121 | 12
0.0114 | 11
0.0108 | 11
0.0105 | 11
0.0104 | 10
0.0099 | 10
0.0094 | 9
0.0093 | 9
0.0084 | 8
0.0082 | 8
0.0081 | 8
0.008 | 8
0.008 | 8
0.0076 | 8
0.0064 | 6
0.0063 | 6
0.0062 | 6
0.0059 | 6
0.0058 | 6
0.0057 | 6
0.0049 | 5
0.0048 | 5
0.0047 | 5
0.0045 | 5
0.0035 | 4
0.0027 | 3
0.0026 | 3
0.0023 | 2
0.0022 | 2
0.0021 | 2
0.0016 | 2
0.0015 | 2
0.001 | 1
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0002 | 0
0.0001 | 0
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## ERV Power During Testing
Time Bucket (America/New_York) | 120 Subpanel-Other-ERV (kWatts)
2023-12-12 13:01 | 0.0866
2023-12-12 13:02 | 0.0871
2023-12-12 13:03 | 0.0873
2023-12-12 13:04 | 0.0869
2023-12-12 13:05 | 0.0871
2023-12-12 13:06 | 0.087
2023-12-12 13:07 | 0.0873
2023-12-12 13:08 | 0.0871
2023-12-12 13:09 | 0.0869
2023-12-12 13:10 | 0.0863
2023-12-12 13:11 | 0.0867
2023-12-12 13:12 | 0.0867
2023-12-12 13:13 | 0.0867
2023-12-12 13:14 | 0.0868
2023-12-12 13:15 | 0.0874
2023-12-12 13:16 | 0.0867
2023-12-12 13:17 | 0.0872
2023-12-12 13:18 | 0.0867
2023-12-12 13:19 | 0.0864
2023-12-12 13:20 | 0.0865
2023-12-12 13:21 | 0.0871
2023-12-12 13:22 | 0.0864
2023-12-12 13:23 | 0.0865
2023-12-12 13:24 | 0.0863
2023-12-12 13:25 | 0.0865
2023-12-12 13:26 | 0.0864
2023-12-12 13:27 | 0.0862
2023-12-12 13:28 | 0.086
2023-12-12 13:29 | 0.0867
2023-12-12 13:30 | 0.0872
2023-12-12 13:31 | 0.0872
2023-12-12 13:32 | 0.0871
2023-12-12 13:33 | 0.0869
2023-12-12 13:34 | 0.0866
2023-12-12 13:35 | 0.0874
2023-12-12 13:36 | 0.087
2023-12-12 13:37 | 0.0871
2023-12-12 13:38 | 0.0873
2023-12-12 13:39 | 0.0874
2023-12-12 13:40 | 0.0872
2023-12-12 13:41 | 0.087
2023-12-12 13:42 | 0.0867
2023-12-12 13:43 | 0.0867
2023-12-12 13:44 | 0.087
2023-12-12 13:45 | 0.087
2023-12-12 13:46 | 0.0868
2023-12-12 13:47 | 0.0867
2023-12-12 13:48 | 0.0871
2023-12-12 13:49 | 0.0868
2023-12-12 13:50 | 0.0868
2023-12-12 13:51 | 0.087
2023-12-12 13:52 | 0.0864
2023-12-12 13:53 | 0.0865
2023-12-12 13:54 | 0.0868
2023-12-12 13:55 | 0.0866
2023-12-12 13:56 | 0.0869
2023-12-12 13:57 | 0.0866
2023-12-12 13:58 | 0.0863
2023-12-12 13:59 | 0.0868
2023-12-12 14:00 | 0.0864
2023-12-12 14:01 | 0.0864
2023-12-12 14:02 | 0.0867
2023-12-12 14:03 | 0.0868
2023-12-12 14:04 | 0.0866
2023-12-12 14:05 | 0.0864
2023-12-12 14:06 | 0.0868
2023-12-12 14:07 | 0.0867
2023-12-12 14:08 | 0.0866
2023-12-12 14:09 | 0.0867
2023-12-12 14:10 | 0.0868
2023-12-12 14:11 | 0.0869
2023-12-12 14:12 | 0.087
2023-12-12 14:13 | 0.0867
2023-12-12 14:14 | 0.0869
2023-12-12 14:15 | 0.0863
2023-12-12 14:16 | 0.0866
2023-12-12 14:17 | 0.0866
2023-12-12 14:18 | 0.0868
2023-12-12 14:19 | 0.0867
2023-12-12 14:20 | 0.0863
2023-12-12 14:21 | 0.0866
2023-12-12 14:22 | 0.0868
2023-12-12 14:23 | 0.0863
2023-12-12 14:24 | 0.0231
2023-12-12 14:25 | 0
2023-12-12 14:26 | 0
2023-12-12 14:27 | 0
2023-12-12 14:28 | 0
2023-12-12 14:29 | 0
2023-12-12 14:30 | 0
2023-12-12 14:31 | 0
2023-12-12 14:32 | 0
2023-12-12 14:33 | 0
2023-12-12 14:34 | 0
2023-12-12 14:35 | 0
2023-12-12 14:36 | 0
2023-12-12 14:37 | 0
2023-12-12 14:38 | 0
2023-12-12 14:39 | 0
2023-12-12 14:40 | 0
2023-12-12 14:41 | 0
2023-12-12 14:42 | 0
2023-12-12 14:43 | 0
2023-12-12 14:44 | 0
2023-12-12 14:45 | 0
2023-12-12 14:46 | 0
2023-12-12 14:47 | 0
2023-12-12 14:48 | 0
2023-12-12 14:49 | 0
2023-12-12 14:50 | 0
2023-12-12 14:51 | 0
2023-12-12 14:52 | 0
2023-12-12 14:53 | 0
2023-12-12 14:54 | 0
2023-12-12 14:55 | 0
2023-12-12 14:56 | 0
2023-12-12 14:57 | 0
2023-12-12 14:58 | 0
2023-12-12 14:59 | 0
2023-12-12 15:00 | 0
2023-12-12 15:01 | 0
2023-12-12 15:02 | 0
2023-12-12 15:03 | 0
2023-12-12 15:04 | 0
2023-12-12 15:05 | 0
2023-12-12 15:06 | 0.0457
2023-12-12 15:07 | 0.0855
2023-12-12 15:08 | 0.086
2023-12-12 15:09 | 0.0858
2023-12-12 15:10 | 0.0862
2023-12-12 15:11 | 0.0863
2023-12-12 15:12 | 0.0861
2023-12-12 15:13 | 0.0859
2023-12-12 15:14 | 0.0859
2023-12-12 15:15 | 0.0856
2023-12-12 15:16 | 0.0861
2023-12-12 15:17 | 0.0857
2023-12-12 15:18 | 0.0859
2023-12-12 15:19 | 0.0859
2023-12-12 15:20 | 0.0862
2023-12-12 15:21 | 0.0867
2023-12-12 15:22 | 0.0864
2023-12-12 15:23 | 0.0861
2023-12-12 15:24 | 0.0572
2023-12-12 15:25 | 0
2023-12-12 15:26 | 0
2023-12-12 15:27 | 0
2023-12-12 15:28 | 0
2023-12-12 15:29 | 0
2023-12-12 15:30 | 0
2023-12-12 15:31 | 0
2023-12-12 15:32 | 0
2023-12-12 15:33 | 0
2023-12-12 15:34 | 0
2023-12-12 15:35 | 0
2023-12-12 15:36 | 0
2023-12-12 15:37 | 0
2023-12-12 15:38 | 0
2023-12-12 15:39 | 0
2023-12-12 15:40 | 0
2023-12-12 15:41 | 0
2023-12-12 15:42 | 0
2023-12-12 15:43 | 0
2023-12-12 15:44 | 0
2023-12-12 15:45 | 0
2023-12-12 15:46 | 0
2023-12-12 15:47 | 0
2023-12-12 15:48 | 0
2023-12-12 15:49 | 0
2023-12-12 15:50 | 0
2023-12-12 15:51 | 0
2023-12-12 15:52 | 0
2023-12-12 15:53 | 0
2023-12-12 15:54 | 0
2023-12-12 15:55 | 0
2023-12-12 15:56 | 0
2023-12-12 15:57 | 0
2023-12-12 15:58 | 0
2023-12-12 15:59 | 0
2023-12-12 16:00 | 0
2023-12-12 16:01 | 0
2023-12-12 16:02 | 0
2023-12-12 16:03 | 0
2023-12-12 16:04 | 0
2023-12-12 16:05 | 0
2023-12-12 16:06 | 0.0185
2023-12-12 16:07 | 0.0846
2023-12-12 16:08 | 0.0853
2023-12-12 16:09 | 0.0853
2023-12-12 16:10 | 0.0854
2023-12-12 16:11 | 0.0857
2023-12-12 16:12 | 0.0857
2023-12-12 16:13 | 0.086
2023-12-12 16:14 | 0.086
2023-12-12 16:15 | 0.0863
2023-12-12 16:16 | 0.0861
2023-12-12 16:17 | 0.0861
2023-12-12 16:18 | 0.0862
2023-12-12 16:19 | 0.0863
2023-12-12 16:20 | 0.0861
2023-12-12 16:21 | 0.086
2023-12-12 16:22 | 0.0861
2023-12-12 16:23 | 0.0863
2023-12-12 16:24 | 0.0854
2023-12-12 16:25 | 0
2023-12-12 16:26 | 0
2023-12-12 16:27 | 0
2023-12-12 16:28 | 0
2023-12-12 16:29 | 0
2023-12-12 16:30 | 0
2023-12-12 16:31 | 0
2023-12-12 16:32 | 0
2023-12-12 16:33 | 0
2023-12-12 16:34 | 0
2023-12-12 16:35 | 0
2023-12-12 16:36 | 0
2023-12-12 16:37 | 0
2023-12-12 16:38 | 0
2023-12-12 16:39 | 0
2023-12-12 16:40 | 0
2023-12-12 16:41 | 0
2023-12-12 16:42 | 0
2023-12-12 16:43 | 0
2023-12-12 16:44 | 0
2023-12-12 16:45 | 0
2023-12-12 16:46 | 0
2023-12-12 16:47 | 0
2023-12-12 16:48 | 0
2023-12-12 16:49 | 0
2023-12-12 16:50 | 0
2023-12-12 16:51 | 0
2023-12-12 16:52 | 0
2023-12-12 16:53 | 0
2023-12-12 16:54 | 0
2023-12-12 16:55 | 0
2023-12-12 16:56 | 0
2023-12-12 16:57 | 0
2023-12-12 16:58 | 0
2023-12-12 16:59 | 0
2023-12-12 17:00 | 0
2023-12-12 17:01 | 0
2023-12-12 17:02 | 0
2023-12-12 17:03 | 0
2023-12-12 17:04 | 0
2023-12-12 17:05 | 0
2023-12-12 17:06 | 0
2023-12-12 17:07 | 0.0718
2023-12-12 17:08 | 0.0862
2023-12-12 17:09 | 0.0865
2023-12-12 17:10 | 0.0855
2023-12-12 17:11 | 0.0854
2023-12-12 17:12 | 0.0869
2023-12-12 17:13 | 0.0866
2023-12-12 17:14 | 0.0866
2023-12-12 17:15 | 0.0869
2023-12-12 17:16 | 0.0869
2023-12-12 17:17 | 0.0869
2023-12-12 17:18 | 0.0869
2023-12-12 17:19 | 0.0872
2023-12-12 17:20 | 0.087
2023-12-12 17:21 | 0.0869
2023-12-12 17:22 | 0.0869
2023-12-12 17:23 | 0.087
2023-12-12 17:24 | 0.0869
2023-12-12 17:25 | 0.0309
2023-12-12 17:26 | 0
2023-12-12 17:27 | 0
2023-12-12 17:28 | 0
2023-12-12 17:29 | 0
2023-12-12 17:30 | 0
2023-12-12 17:31 | 0
2023-12-12 17:32 | 0
2023-12-12 17:33 | 0
2023-12-12 17:34 | 0
2023-12-12 17:35 | 0
2023-12-12 17:36 | 0
2023-12-12 17:37 | 0
2023-12-12 17:38 | 0.0014
2023-12-12 17:39 | 0.0856
2023-12-12 17:40 | 0.0863
2023-12-12 17:41 | 0.0869
2023-12-12 17:42 | 0.087
2023-12-12 17:43 | 0.0867
2023-12-12 17:44 | 0.0868
2023-12-12 17:45 | 0.0868
2023-12-12 17:46 | 0.0867
2023-12-12 17:47 | 0.0866
2023-12-12 17:48 | 0.0864
2023-12-12 17:49 | 0.0866
2023-12-12 17:50 | 0.0864
2023-12-12 17:51 | 0.0865
2023-12-12 17:52 | 0.0864
2023-12-12 17:53 | 0.0867
2023-12-12 17:54 | 0.0867
2023-12-12 17:55 | 0.0868
2023-12-12 17:56 | 0.0868
2023-12-12 17:57 | 0.0869
2023-12-12 17:58 | 0.0871
2023-12-12 17:59 | 0.0871
2023-12-12 18:00 | 0.0868
2023-12-12 18:01 | 0.0871
2023-12-12 18:02 | 0.0866
2023-12-12 18:03 | 0.0865
2023-12-12 18:04 | 0.0865
2023-12-12 18:05 | 0.0863
2023-12-12 18:06 | 0.0864
2023-12-12 18:07 | 0.0863
2023-12-12 18:08 | 0.0862
2023-12-12 18:09 | 0.0861
2023-12-12 18:10 | 0.0861
2023-12-12 18:11 | 0.0863
2023-12-12 18:12 | 0.0863
2023-12-12 18:13 | 0.0862
2023-12-12 18:14 | 0.0863
2023-12-12 18:15 | 0.0866
2023-12-12 18:16 | 0.0866
2023-12-12 18:17 | 0.0866
2023-12-12 18:18 | 0.0867
2023-12-12 18:19 | 0.0868
2023-12-12 18:20 | 0.0868
2023-12-12 18:21 | 0.0865
2023-12-12 18:22 | 0.0864
2023-12-12 18:23 | 0.0862
2023-12-12 18:24 | 0.0862
2023-12-12 18:25 | 0.0864
2023-12-12 18:26 | 0.0861
2023-12-12 18:27 | 0.086
2023-12-12 18:28 | 0.0863
2023-12-12 18:29 | 0.0863
2023-12-12 18:30 | 0.0862
2023-12-12 18:31 | 0.0865
2023-12-12 18:32 | 0.0865
2023-12-12 18:33 | 0.0337
2023-12-12 18:34 | 0
2023-12-12 18:35 | 0
2023-12-12 18:36 | 0
2023-12-12 18:37 | 0
2023-12-12 18:38 | 0
2023-12-12 18:39 | 0.0555
2023-12-12 18:40 | 0.0861
2023-12-12 18:41 | 0.0861
2023-12-12 18:42 | 0.0863
2023-12-12 18:43 | 0.0864
2023-12-12 18:44 | 0.0864
2023-12-12 18:45 | 0.0862
2023-12-12 18:46 | 0.0861
2023-12-12 18:47 | 0.0863
2023-12-12 18:48 | 0.086
2023-12-12 18:49 | 0.0861
2023-12-12 18:50 | 0.0862
2023-12-12 18:51 | 0.0861
2023-12-12 18:52 | 0.0864
2023-12-12 18:53 | 0.0864
2023-12-12 18:54 | 0.0861
2023-12-12 18:55 | 0.0863
2023-12-12 18:56 | 0.0864
2023-12-12 18:57 | 0.0863
2023-12-12 18:58 | 0.0864
2023-12-12 18:59 | 0.0863
2023-12-12 19:00 | 0.0863
2023-12-12 19:01 | 0.0864
2023-12-12 19:02 | 0.0866
2023-12-12 19:03 | 0.0864
2023-12-12 19:04 | 0.0862
2023-12-12 19:05 | 0.0865
2023-12-12 19:06 | 0.0862
2023-12-12 19:07 | 0.0861
2023-12-12 19:08 | 0.0861
2023-12-12 19:09 | 0.086
2023-12-12 19:10 | 0.0863
2023-12-12 19:11 | 0.0862
2023-12-12 19:12 | 0.0861
2023-12-12 19:13 | 0.0863
2023-12-12 19:14 | 0.0863
2023-12-12 19:15 | 0.0866
2023-12-12 19:16 | 0.0864
2023-12-12 19:17 | 0.0864
2023-12-12 19:18 | 0.086
2023-12-12 19:19 | 0.086
2023-12-12 19:20 | 0.0863
2023-12-12 19:21 | 0.0866
2023-12-12 19:22 | 0.0863
2023-12-12 19:23 | 0.0863
2023-12-12 19:24 | 0.0865
2023-12-12 19:25 | 0.0864
2023-12-12 19:26 | 0.0864
2023-12-12 19:27 | 0.0864
2023-12-12 19:28 | 0.0864
2023-12-12 19:29 | 0.0868
2023-12-12 19:30 | 0.0863
2023-12-12 19:31 | 0.086
2023-12-12 19:32 | 0.0863
2023-12-12 19:33 | 0.0612
2023-12-12 19:34 | 0
2023-12-12 19:35 | 0
2023-12-12 19:36 | 0
2023-12-12 19:37 | 0
2023-12-12 19:38 | 0
2023-12-12 19:39 | 0.0284
2023-12-12 19:40 | 0.0856
2023-12-12 19:41 | 0.0863
2023-12-12 19:42 | 0.0863
2023-12-12 19:43 | 0.0861
2023-12-12 19:44 | 0.0861
2023-12-12 19:45 | 0.086
2023-12-12 19:46 | 0.0862
2023-12-12 19:47 | 0.0864
2023-12-12 19:48 | 0.0866
2023-12-12 19:49 | 0.0861
2023-12-12 19:50 | 0.0844
2023-12-12 19:51 | 0.0843
2023-12-12 19:52 | 0.0857
2023-12-12 19:53 | 0.0857
2023-12-12 19:54 | 0.0858
2023-12-12 19:55 | 0.0843
2023-12-12 19:56 | 0.0846
2023-12-12 19:57 | 0.0848
2023-12-12 19:58 | 0.0844
2023-12-12 19:59 | 0.0846
2023-12-12 20:00 | 0.0845
2023-12-12 20:01 | 0.0846
2023-12-12 20:02 | 0.0847
2023-12-12 20:03 | 0.0847
2023-12-12 20:04 | 0.0846
2023-12-12 20:05 | 0.0848
2023-12-12 20:06 | 0.0848
2023-12-12 20:07 | 0.0847
2023-12-12 20:08 | 0.0847
2023-12-12 20:09 | 0.0855
2023-12-12 20:10 | 0.0858
2023-12-12 20:11 | 0.0861
2023-12-12 20:12 | 0.0852
2023-12-12 20:13 | 0.0845
2023-12-12 20:14 | 0.0855
2023-12-12 20:15 | 0.0861
2023-12-12 20:16 | 0.0862
2023-12-12 20:17 | 0.0846
2023-12-12 20:18 | 0.0846
2023-12-12 20:19 | 0.0851
2023-12-12 20:20 | 0.0845
2023-12-12 20:21 | 0.0847
2023-12-12 20:22 | 0.0848
2023-12-12 20:23 | 0.0848
2023-12-12 20:24 | 0.0849
2023-12-12 20:25 | 0.0849
2023-12-12 20:26 | 0.0852
2023-12-12 20:27 | 0.0851
2023-12-12 20:28 | 0.0849
2023-12-12 20:29 | 0.0851
2023-12-12 20:30 | 0.0848
2023-12-12 20:31 | 0.085
2023-12-12 20:32 | 0.0849
2023-12-12 20:33 | 0.0847
2023-12-12 20:34 | 0
2023-12-12 20:35 | 0
2023-12-12 20:36 | 0
2023-12-12 20:37 | 0
2023-12-12 20:38 | 0
2023-12-12 20:39 | 0
2023-12-12 20:40 | 0.0909
2023-12-12 20:41 | 0.0847
2023-12-12 20:42 | 0.0854
2023-12-12 20:43 | 0.0863
2023-12-12 20:44 | 0.0866
2023-12-12 20:45 | 0.0866
2023-12-12 20:46 | 0.0864
2023-12-12 20:47 | 0.0863
2023-12-12 20:48 | 0.0865
2023-12-12 20:49 | 0.0867
2023-12-12 20:50 | 0.0865
2023-12-12 20:51 | 0.0868
2023-12-12 20:52 | 0.0866
2023-12-12 20:53 | 0.0868
2023-12-12 20:54 | 0.0865
2023-12-12 20:55 | 0.0867
2023-12-12 20:56 | 0.0865
2023-12-12 20:57 | 0.0866
2023-12-12 20:58 | 0.0865
2023-12-12 20:59 | 0.0867
2023-12-12 21:00 | 0.0864
2023-12-12 21:01 | 0.0865
2023-12-12 21:02 | 0.0862
2023-12-12 21:03 | 0.0865
2023-12-12 21:04 | 0.0868
2023-12-12 21:05 | 0.0866
2023-12-12 21:06 | 0.0864
2023-12-12 21:07 | 0.0865
2023-12-12 21:08 | 0.0867
2023-12-12 21:09 | 0.0863
2023-12-12 21:10 | 0.0862
2023-12-12 21:11 | 0.0863
2023-12-12 21:12 | 0.0865
2023-12-12 21:13 | 0.0864
2023-12-12 21:14 | 0.0864
2023-12-12 21:15 | 0.0864
2023-12-12 21:16 | 0.0864
2023-12-12 21:17 | 0.0867
2023-12-12 21:18 | 0.0866
2023-12-12 21:19 | 0.0869
2023-12-12 21:20 | 0.0866
2023-12-12 21:21 | 0.0865
2023-12-12 21:22 | 0.0869
2023-12-12 21:23 | 0.0868
2023-12-12 21:24 | 0.087
2023-12-12 21:25 | 0.0869
2023-12-12 21:26 | 0.0871
2023-12-12 21:27 | 0.0869
2023-12-12 21:28 | 0.087
2023-12-12 21:29 | 0.087
2023-12-12 21:30 | 0.0876
2023-12-12 21:31 | 0.0872
2023-12-12 21:32 | 0.0867
2023-12-12 21:33 | 0.0869
2023-12-12 21:34 | 0.0218
2023-12-12 21:35 | 0
2023-12-12 21:36 | 0
2023-12-12 21:37 | 0
2023-12-12 21:38 | 0
2023-12-12 21:39 | 0
2023-12-12 21:40 | 0.0688
2023-12-12 21:41 | 0.0869
2023-12-12 21:42 | 0.0869
2023-12-12 21:43 | 0.0874
2023-12-12 21:44 | 0.0873
2023-12-12 21:45 | 0.0871
2023-12-12 21:46 | 0.0872
2023-12-12 21:47 | 0.0867
2023-12-12 21:48 | 0.0872
2023-12-12 21:49 | 0.0874
2023-12-12 21:50 | 0.0871
2023-12-12 21:51 | 0.0874
2023-12-12 21:52 | 0.0873
2023-12-12 21:53 | 0.0873
2023-12-12 21:54 | 0.0872
2023-12-12 21:55 | 0.0871
2023-12-12 21:56 | 0.0873
2023-12-12 21:57 | 0.087
2023-12-12 21:58 | 0.087
2023-12-12 21:59 | 0.0871
2023-12-12 22:00 | 0.0873
2023-12-12 22:01 | 0.0871
2023-12-12 22:02 | 0.0871
2023-12-12 22:03 | 0.087
2023-12-12 22:04 | 0.087
2023-12-12 22:05 | 0.0873
2023-12-12 22:06 | 0.0872
2023-12-12 22:07 | 0.0874
2023-12-12 22:08 | 0.0875
2023-12-12 22:09 | 0.0875
2023-12-12 22:10 | 0.0869
2023-12-12 22:11 | 0.0873
2023-12-12 22:12 | 0.0873
2023-12-12 22:13 | 0.0874
2023-12-12 22:14 | 0.0874
2023-12-12 22:15 | 0.0874
2023-12-12 22:16 | 0.0871
2023-12-12 22:17 | 0.0871
2023-12-12 22:18 | 0.0872
2023-12-12 22:19 | 0.0871
2023-12-12 22:20 | 0.0871
2023-12-12 22:21 | 0.0872
2023-12-12 22:22 | 0.0871
2023-12-12 22:23 | 0.0872
2023-12-12 22:24 | 0.0869
2023-12-12 22:25 | 0.0871
2023-12-12 22:26 | 0.0871
2023-12-12 22:27 | 0.0871
2023-12-12 22:28 | 0.0872
2023-12-12 22:29 | 0.0874
2023-12-12 22:30 | 0.087
2023-12-12 22:31 | 0.0864
2023-12-12 22:32 | 0.0869
2023-12-12 22:33 | 0.087
2023-12-12 22:34 | 0.0399
2023-12-12 22:35 | 0
2023-12-12 22:36 | 0
2023-12-12 22:37 | 0
2023-12-12 22:38 | 0
2023-12-12 22:39 | 0.0008
2023-12-12 22:40 | 0.0506
2023-12-12 22:41 | 0.0865
2023-12-12 22:42 | 0.0868
2023-12-12 22:43 | 0.0869
2023-12-12 22:44 | 0.087
2023-12-12 22:45 | 0.0868
2023-12-12 22:46 | 0.0868
2023-12-12 22:47 | 0.087
2023-12-12 22:48 | 0.0867
2023-12-12 22:49 | 0.087
2023-12-12 22:50 | 0.087
2023-12-12 22:51 | 0.0871
2023-12-12 22:52 | 0.0873
2023-12-12 22:53 | 0.087
2023-12-12 22:54 | 0.0871
2023-12-12 22:55 | 0.087
2023-12-12 22:56 | 0.0872
2023-12-12 22:57 | 0.0866
2023-12-12 22:58 | 0.087
2023-12-12 22:59 | 0.087
2023-12-12 23:00 | 0.0871
2023-12-12 23:01 | 0.0869
2023-12-12 23:02 | 0.0872
2023-12-12 23:03 | 0.0871
2023-12-12 23:04 | 0.0866
2023-12-12 23:05 | 0.0861
2023-12-12 23:06 | 0.0867
2023-12-12 23:07 | 0.0864
2023-12-12 23:08 | 0.0866
2023-12-12 23:09 | 0.0866
2023-12-12 23:10 | 0.0867
2023-12-12 23:11 | 0.0868
2023-12-12 23:12 | 0.0871
2023-12-12 23:13 | 0.0868
2023-12-12 23:14 | 0.0869
2023-12-12 23:15 | 0.0869
2023-12-12 23:16 | 0.0867
2023-12-12 23:17 | 0.0868
2023-12-12 23:18 | 0.0868
2023-12-12 23:19 | 0.0866
2023-12-12 23:20 | 0.0867
2023-12-12 23:21 | 0.0867
2023-12-12 23:22 | 0.0869
2023-12-12 23:23 | 0.0869
2023-12-12 23:24 | 0.0869
2023-12-12 23:25 | 0.0865
2023-12-12 23:26 | 0.0866
2023-12-12 23:27 | 0.0868
2023-12-12 23:28 | 0.0868
2023-12-12 23:29 | 0.0867
2023-12-12 23:30 | 0.0867
2023-12-12 23:31 | 0.0868
2023-12-12 23:32 | 0.087
2023-12-12 23:33 | 0.0867
2023-12-12 23:34 | 0.0504
2023-12-12 23:35 | 0
2023-12-12 23:36 | 0
2023-12-12 23:37 | 0
2023-12-12 23:38 | 0
2023-12-12 23:39 | 0
2023-12-12 23:40 | 0.0419
2023-12-12 23:41 | 0.0867
2023-12-12 23:42 | 0.0868
2023-12-12 23:43 | 0.0868
2023-12-12 23:44 | 0.0869
2023-12-12 23:45 | 0.087
2023-12-12 23:46 | 0.0873
2023-12-12 23:47 | 0.0871
2023-12-12 23:48 | 0.0872
2023-12-12 23:49 | 0.0874
2023-12-12 23:50 | 0.0871
2023-12-12 23:51 | 0.0873
2023-12-12 23:52 | 0.0871
2023-12-12 23:53 | 0.0867
2023-12-12 23:54 | 0.0871
2023-12-12 23:55 | 0.0872
2023-12-12 23:56 | 0.0871
2023-12-12 23:57 | 0.0872
2023-12-12 23:58 | 0.0872
2023-12-12 23:59 | 0.0877
2023-12-13 | 0.0873
2023-12-13 00:01 | 0.0873
2023-12-13 00:02 | 0.0873
2023-12-13 00:03 | 0.0875
2023-12-13 00:04 | 0.0872
2023-12-13 00:05 | 0.0874
2023-12-13 00:06 | 0.0873
2023-12-13 00:07 | 0.0873
2023-12-13 00:08 | 0.0874
2023-12-13 00:09 | 0.0872
2023-12-13 00:10 | 0.0871
2023-12-13 00:11 | 0.0871
2023-12-13 00:12 | 0.0873
2023-12-13 00:13 | 0.0876
2023-12-13 00:14 | 0.0872
2023-12-13 00:15 | 0.0874
2023-12-13 00:16 | 0.0874
2023-12-13 00:17 | 0.0873
2023-12-13 00:18 | 0.0874
2023-12-13 00:19 | 0.0875
2023-12-13 00:20 | 0.0873
2023-12-13 00:21 | 0.0874
2023-12-13 00:22 | 0.0877
2023-12-13 00:23 | 0.0875
2023-12-13 00:24 | 0.0874
2023-12-13 00:25 | 0.0875
2023-12-13 00:26 | 0.0875
2023-12-13 00:27 | 0.0876
2023-12-13 00:28 | 0.0871
2023-12-13 00:29 | 0.0873
2023-12-13 00:30 | 0.0872
2023-12-13 00:31 | 0.0872
2023-12-13 00:32 | 0.0872
2023-12-13 00:33 | 0.087
2023-12-13 00:34 | 0.0566
2023-12-13 00:35 | 0
2023-12-13 00:36 | 0
2023-12-13 00:37 | 0
2023-12-13 00:38 | 0
2023-12-13 00:39 | 0
2023-12-13 00:40 | 0.0363
2023-12-13 00:41 | 0.0868
2023-12-13 00:42 | 0.0872
2023-12-13 00:43 | 0.0876
2023-12-13 00:44 | 0.0875
2023-12-13 00:45 | 0.0874
2023-12-13 00:46 | 0.0875
2023-12-13 00:47 | 0.0878
2023-12-13 00:48 | 0.0874
2023-12-13 00:49 | 0.0872
2023-12-13 00:50 | 0.0874
2023-12-13 00:51 | 0.0876
2023-12-13 00:52 | 0.0876
2023-12-13 00:53 | 0.0874
2023-12-13 00:54 | 0.0876
2023-12-13 00:55 | 0.0874
2023-12-13 00:56 | 0.0875
2023-12-13 00:57 | 0.0874
2023-12-13 00:58 | 0.0869
2023-12-13 00:59 | 0.0871
2023-12-13 01:00 | 0.087
2023-12-13 01:01 | 0.0872
2023-12-13 01:02 | 0.0874
2023-12-13 01:03 | 0.0873
2023-12-13 01:04 | 0.0874
2023-12-13 01:05 | 0.0875
2023-12-13 01:06 | 0.0876
2023-12-13 01:07 | 0.0875
2023-12-13 01:08 | 0.0877
2023-12-13 01:09 | 0.0876
2023-12-13 01:10 | 0.0876
2023-12-13 01:11 | 0.0879
2023-12-13 01:12 | 0.0873
2023-12-13 01:13 | 0.0876
2023-12-13 01:14 | 0.0873
2023-12-13 01:15 | 0.0873
2023-12-13 01:16 | 0.0873
2023-12-13 01:17 | 0.0873
2023-12-13 01:18 | 0.0874
2023-12-13 01:19 | 0.0874
2023-12-13 01:20 | 0.0872
2023-12-13 01:21 | 0.0871
2023-12-13 01:22 | 0.0872
2023-12-13 01:23 | 0.0872
2023-12-13 01:24 | 0.0872
2023-12-13 01:25 | 0.0873
2023-12-13 01:26 | 0.087
2023-12-13 01:27 | 0.0872
2023-12-13 01:28 | 0.0874
2023-12-13 01:29 | 0.0875
2023-12-13 01:30 | 0.0877
2023-12-13 01:31 | 0.0876
2023-12-13 01:32 | 0.0876
2023-12-13 01:33 | 0.0875
2023-12-13 01:34 | 0.0591
2023-12-13 01:35 | 0
2023-12-13 01:36 | 0
2023-12-13 01:37 | 0
2023-12-13 01:38 | 0
2023-12-13 01:39 | 0
2023-12-13 01:40 | 0.0345
2023-12-13 01:41 | 0.0867
2023-12-13 01:42 | 0.0871
2023-12-13 01:43 | 0.0872
2023-12-13 01:44 | 0.0872
2023-12-13 01:45 | 0.0873
2023-12-13 01:46 | 0.0875
2023-12-13 01:47 | 0.0873
2023-12-13 01:48 | 0.0875
2023-12-13 01:49 | 0.0877
2023-12-13 01:50 | 0.0877
2023-12-13 01:51 | 0.0877
2023-12-13 01:52 | 0.0876
2023-12-13 01:53 | 0.0876
2023-12-13 01:54 | 0.0877
2023-12-13 01:55 | 0.0876
2023-12-13 01:56 | 0.0877
2023-12-13 01:57 | 0.0877
2023-12-13 01:58 | 0.0877
2023-12-13 01:59 | 0.0876
2023-12-13 02:00 | 0.0879
2023-12-13 02:01 | 0.0877
2023-12-13 02:02 | 0.0873
2023-12-13 02:03 | 0.0871
2023-12-13 02:04 | 0.0872
2023-12-13 02:05 | 0.0874
2023-12-13 02:06 | 0.0876
2023-12-13 02:07 | 0.0873
2023-12-13 02:08 | 0.0877
2023-12-13 02:09 | 0.0878
2023-12-13 02:10 | 0.0878
2023-12-13 02:11 | 0.0877
2023-12-13 02:12 | 0.0877
2023-12-13 02:13 | 0.0878
2023-12-13 02:14 | 0.0877
2023-12-13 02:15 | 0.0875
2023-12-13 02:16 | 0.0879
2023-12-13 02:17 | 0.0877
2023-12-13 02:18 | 0.0873
2023-12-13 02:19 | 0.0875
2023-12-13 02:20 | 0.0873
2023-12-13 02:21 | 0.0875
2023-12-13 02:22 | 0.0874
2023-12-13 02:23 | 0.0872
2023-12-13 02:24 | 0.0875
2023-12-13 02:25 | 0.0876
2023-12-13 02:26 | 0.0873
2023-12-13 02:27 | 0.0875
2023-12-13 02:28 | 0.0877
2023-12-13 02:29 | 0.0877
2023-12-13 02:30 | 0.0878
2023-12-13 02:31 | 0.0875
2023-12-13 02:32 | 0.0874
2023-12-13 02:33 | 0.0875
2023-12-13 02:34 | 0.0571
2023-12-13 02:35 | 0
2023-12-13 02:36 | 0
2023-12-13 02:37 | 0
2023-12-13 02:38 | 0
2023-12-13 02:39 | 0
2023-12-13 02:40 | 0.0368
2023-12-13 02:41 | 0.0867
2023-12-13 02:42 | 0.0871
2023-12-13 02:43 | 0.0871
2023-12-13 02:44 | 0.0868
2023-12-13 02:45 | 0.087
2023-12-13 02:46 | 0.0868
2023-12-13 02:47 | 0.087
2023-12-13 02:48 | 0.0866
2023-12-13 02:49 | 0.0867
2023-12-13 02:50 | 0.0868
2023-12-13 02:51 | 0.0872
2023-12-13 02:52 | 0.087
2023-12-13 02:53 | 0.0873
2023-12-13 02:54 | 0.0871
2023-12-13 02:55 | 0.0874
2023-12-13 02:56 | 0.0876
2023-12-13 02:57 | 0.0878
2023-12-13 02:58 | 0.0878
2023-12-13 02:59 | 0.0877
2023-12-13 03:00 | 0.0878
2023-12-13 03:01 | 0.0879
2023-12-13 03:02 | 0.0878
2023-12-13 03:03 | 0.0876
2023-12-13 03:04 | 0.0879
2023-12-13 03:05 | 0.0877
2023-12-13 03:06 | 0.0878
2023-12-13 03:07 | 0.0877
2023-12-13 03:08 | 0.0875
2023-12-13 03:09 | 0.0876
2023-12-13 03:10 | 0.0872
2023-12-13 03:11 | 0.0874
2023-12-13 03:12 | 0.0877
2023-12-13 03:13 | 0.0879
2023-12-13 03:14 | 0.0875
2023-12-13 03:15 | 0.0877
2023-12-13 03:16 | 0.0876
2023-12-13 03:17 | 0.0876
2023-12-13 03:18 | 0.0876
2023-12-13 03:19 | 0.0877
2023-12-13 03:20 | 0.0879
2023-12-13 03:21 | 0.0877
2023-12-13 03:22 | 0.0876
2023-12-13 03:23 | 0.0877
2023-12-13 03:24 | 0.0876
2023-12-13 03:25 | 0.0877
2023-12-13 03:26 | 0.0873
2023-12-13 03:27 | 0.0875
2023-12-13 03:28 | 0.0876
2023-12-13 03:29 | 0.0875
2023-12-13 03:30 | 0.0875
2023-12-13 03:31 | 0.0875
2023-12-13 03:32 | 0.0876
2023-12-13 03:33 | 0.0875
2023-12-13 03:34 | 0.0508
2023-12-13 03:35 | 0
2023-12-13 03:36 | 0
2023-12-13 03:37 | 0
2023-12-13 03:38 | 0
2023-12-13 03:39 | 0
2023-12-13 03:40 | 0.0439
2023-12-13 03:41 | 0.0874
2023-12-13 03:42 | 0.0874
2023-12-13 03:43 | 0.0876
2023-12-13 03:44 | 0.0877
2023-12-13 03:45 | 0.0879
2023-12-13 03:46 | 0.0877
2023-12-13 03:47 | 0.0876
2023-12-13 03:48 | 0.0878
2023-12-13 03:49 | 0.0876
2023-12-13 03:50 | 0.0876
2023-12-13 03:51 | 0.0877
2023-12-13 03:52 | 0.0876
2023-12-13 03:53 | 0.0876
2023-12-13 03:54 | 0.0877
2023-12-13 03:55 | 0.0877
2023-12-13 03:56 | 0.0876
2023-12-13 03:57 | 0.0875
2023-12-13 03:58 | 0.0876
2023-12-13 03:59 | 0.0876
2023-12-13 04:00 | 0.0877
2023-12-13 04:01 | 0.0877
2023-12-13 04:02 | 0.0878
2023-12-13 04:03 | 0.0876
2023-12-13 04:04 | 0.0876
2023-12-13 04:05 | 0.0878
2023-12-13 04:06 | 0.0879
2023-12-13 04:07 | 0.0878
2023-12-13 04:08 | 0.0881
2023-12-13 04:09 | 0.0877
2023-12-13 04:10 | 0.0878
2023-12-13 04:11 | 0.088
2023-12-13 04:12 | 0.0877
2023-12-13 04:13 | 0.0876
2023-12-13 04:14 | 0.0877
2023-12-13 04:15 | 0.0874
2023-12-13 04:16 | 0.0877
2023-12-13 04:17 | 0.0876
2023-12-13 04:18 | 0.0874
2023-12-13 04:19 | 0.0875
2023-12-13 04:20 | 0.0874
2023-12-13 04:21 | 0.0874
2023-12-13 04:22 | 0.0875
2023-12-13 04:23 | 0.0877
2023-12-13 04:24 | 0.0875
2023-12-13 04:25 | 0.0878
2023-12-13 04:26 | 0.0877
2023-12-13 04:27 | 0.0876
2023-12-13 04:28 | 0.0878
2023-12-13 04:29 | 0.0878
2023-12-13 04:30 | 0.0875
2023-12-13 04:31 | 0.0877
2023-12-13 04:32 | 0.0877
2023-12-13 04:33 | 0.0875
2023-12-13 04:34 | 0.0406
2023-12-13 04:35 | 0
2023-12-13 04:36 | 0
2023-12-13 04:37 | 0
2023-12-13 04:38 | 0
2023-12-13 04:39 | 0
2023-12-13 04:40 | 0.0542
2023-12-13 04:41 | 0.087
2023-12-13 04:42 | 0.0875
2023-12-13 04:43 | 0.0875
2023-12-13 04:44 | 0.0873
2023-12-13 04:45 | 0.0874
2023-12-13 04:46 | 0.0876
2023-12-13 04:47 | 0.0877
2023-12-13 04:48 | 0.0877
2023-12-13 04:49 | 0.0877
2023-12-13 04:50 | 0.0875
2023-12-13 04:51 | 0.0876
2023-12-13 04:52 | 0.0876
2023-12-13 04:53 | 0.0877
2023-12-13 04:54 | 0.0874
2023-12-13 04:55 | 0.0875
2023-12-13 04:56 | 0.0876
2023-12-13 04:57 | 0.0876
2023-12-13 04:58 | 0.0875
2023-12-13 04:59 | 0.0876
2023-12-13 05:00 | 0.0876
2023-12-13 05:01 | 0.0877
2023-12-13 05:02 | 0.0875
2023-12-13 05:03 | 0.0876
2023-12-13 05:04 | 0.0877
2023-12-13 05:05 | 0.0877
2023-12-13 05:06 | 0.0877
2023-12-13 05:07 | 0.0878
2023-12-13 05:08 | 0.0876
2023-12-13 05:09 | 0.0876
2023-12-13 05:10 | 0.0877
2023-12-13 05:11 | 0.0877
2023-12-13 05:12 | 0.088
2023-12-13 05:13 | 0.0879
2023-12-13 05:14 | 0.0876
2023-12-13 05:15 | 0.0875
2023-12-13 05:16 | 0.0875
2023-12-13 05:17 | 0.0876
2023-12-13 05:18 | 0.0874
2023-12-13 05:19 | 0.0875
2023-12-13 05:20 | 0.0876
2023-12-13 05:21 | 0.0875
2023-12-13 05:22 | 0.0877
2023-12-13 05:23 | 0.0875
2023-12-13 05:24 | 0.0875
2023-12-13 05:25 | 0.0875
2023-12-13 05:26 | 0.0878
2023-12-13 05:27 | 0.0877
2023-12-13 05:28 | 0.088
2023-12-13 05:29 | 0.0876
2023-12-13 05:30 | 0.0876
2023-12-13 05:31 | 0.0876
2023-12-13 05:32 | 0.0876
2023-12-13 05:33 | 0.0876
2023-12-13 05:34 | 0.0259
2023-12-13 05:35 | 0
2023-12-13 05:36 | 0
2023-12-13 05:37 | 0
2023-12-13 05:38 | 0
2023-12-13 05:39 | 0
2023-12-13 05:40 | 0.0701
2023-12-13 05:41 | 0.0868
2023-12-13 05:42 | 0.087
2023-12-13 05:43 | 0.0874
2023-12-13 05:44 | 0.0873
2023-12-13 05:45 | 0.0875
2023-12-13 05:46 | 0.0874
2023-12-13 05:47 | 0.0873
2023-12-13 05:48 | 0.0876
2023-12-13 05:49 | 0.0875
2023-12-13 05:50 | 0.0876
2023-12-13 05:51 | 0.0876
2023-12-13 05:52 | 0.0878
2023-12-13 05:53 | 0.0878
2023-12-13 05:54 | 0.0877
2023-12-13 05:55 | 0.0875
2023-12-13 05:56 | 0.0876
2023-12-13 05:57 | 0.0874
2023-12-13 05:58 | 0.0875
2023-12-13 05:59 | 0.0874
2023-12-13 06:00 | 0.0875
2023-12-13 06:01 | 0.0873
2023-12-13 06:02 | 0.0872
2023-12-13 06:03 | 0.0872
2023-12-13 06:04 | 0.087
2023-12-13 06:05 | 0.0872
2023-12-13 06:06 | 0.0873
2023-12-13 06:07 | 0.0873
2023-12-13 06:08 | 0.0875
2023-12-13 06:09 | 0.0871
2023-12-13 06:10 | 0.0871
2023-12-13 06:11 | 0.0874
2023-12-13 06:12 | 0.0873
2023-12-13 06:13 | 0.0873
2023-12-13 06:14 | 0.0871
2023-12-13 06:15 | 0.0875
2023-12-13 06:16 | 0.0875
2023-12-13 06:17 | 0.0875
2023-12-13 06:18 | 0.0875
2023-12-13 06:19 | 0.0875
2023-12-13 06:20 | 0.0875
2023-12-13 06:21 | 0.0875
2023-12-13 06:22 | 0.0879
2023-12-13 06:23 | 0.0878
2023-12-13 06:24 | 0.0881
2023-12-13 06:25 | 0.0881
2023-12-13 06:26 | 0.0877
2023-12-13 06:27 | 0.0876
2023-12-13 06:28 | 0.0876
2023-12-13 06:29 | 0.0875
2023-12-13 06:30 | 0.0876
2023-12-13 06:31 | 0.0874
2023-12-13 06:32 | 0.0874
2023-12-13 06:33 | 0.0874
2023-12-13 06:34 | 0.0086
2023-12-13 06:35 | 0
2023-12-13 06:36 | 0
2023-12-13 06:37 | 0
2023-12-13 06:38 | 0
2023-12-13 06:39 | 0
2023-12-13 06:40 | 0.0867
2023-12-13 06:41 | 0.087
2023-12-13 06:42 | 0.0873
2023-12-13 06:43 | 0.0872
2023-12-13 06:44 | 0.0871
2023-12-13 06:45 | 0.0874
2023-12-13 06:46 | 0.0871
2023-12-13 06:47 | 0.0871
2023-12-13 06:48 | 0.0869
2023-12-13 06:49 | 0.0864
2023-12-13 06:50 | 0.0865
2023-12-13 06:51 | 0.0867
2023-12-13 06:52 | 0.0867
2023-12-13 06:53 | 0.0865
2023-12-13 06:54 | 0.0869
2023-12-13 06:55 | 0.0869
2023-12-13 06:56 | 0.087
2023-12-13 06:57 | 0.0872
2023-12-13 06:58 | 0.0872
2023-12-13 06:59 | 0.0875
2023-12-13 07:00 | 0.087
2023-12-13 07:01 | 0.087
2023-12-13 07:02 | 0.0871
2023-12-13 07:03 | 0.0869
2023-12-13 07:04 | 0.0868
2023-12-13 07:05 | 0.0868
2023-12-13 07:06 | 0.0867
2023-12-13 07:07 | 0.0871
2023-12-13 07:08 | 0.0868
2023-12-13 07:09 | 0.0868
2023-12-13 07:10 | 0.0868
2023-12-13 07:11 | 0.0871
2023-12-13 07:12 | 0.0868
2023-12-13 07:13 | 0.0868
2023-12-13 07:14 | 0.0867
2023-12-13 07:15 | 0.0867
2023-12-13 07:16 | 0.0869
2023-12-13 07:17 | 0.087
2023-12-13 07:18 | 0.0868
2023-12-13 07:19 | 0.0868
2023-12-13 07:20 | 0.0872
2023-12-13 07:21 | 0.087
2023-12-13 07:22 | 0.0869
2023-12-13 07:23 | 0.087
2023-12-13 07:24 | 0.0869
2023-12-13 07:25 | 0.087
2023-12-13 07:26 | 0.0871
2023-12-13 07:27 | 0.0872
2023-12-13 07:28 | 0.087
2023-12-13 07:29 | 0.0871
2023-12-13 07:30 | 0.0868
2023-12-13 07:31 | 0.087
2023-12-13 07:32 | 0.0869
2023-12-13 07:33 | 0.0802
2023-12-13 07:34 | 0.0069
2023-12-13 07:35 | 0
2023-12-13 07:36 | 0
2023-12-13 07:37 | 0
2023-12-13 07:38 | 0
2023-12-13 07:39 | 0.0021
2023-12-13 07:40 | 0.0911
2023-12-13 07:41 | 0.0865
2023-12-13 07:42 | 0.0866
2023-12-13 07:43 | 0.0867
2023-12-13 07:44 | 0.0865
2023-12-13 07:45 | 0.0864
2023-12-13 07:46 | 0.0867
2023-12-13 07:47 | 0.0868
2023-12-13 07:48 | 0.0868
2023-12-13 07:49 | 0.0868
2023-12-13 07:50 | 0.087
2023-12-13 07:51 | 0.0871
2023-12-13 07:52 | 0.0869
2023-12-13 07:53 | 0.087
2023-12-13 07:54 | 0.0871
2023-12-13 07:55 | 0.0869
2023-12-13 07:56 | 0.0868
2023-12-13 07:57 | 0.0868
2023-12-13 07:58 | 0.0867
2023-12-13 07:59 | 0.0866
2023-12-13 08:00 | 0.0871
2023-12-13 08:01 | 0.087
2023-12-13 08:02 | 0.087
2023-12-13 08:03 | 0.0867
2023-12-13 08:04 | 0.0868
2023-12-13 08:05 | 0.0869
2023-12-13 08:06 | 0.0867
2023-12-13 08:07 | 0.0868
2023-12-13 08:08 | 0.0867
2023-12-13 08:09 | 0.0867
2023-12-13 08:10 | 0.0868
2023-12-13 08:11 | 0.0864
2023-12-13 08:12 | 0.0869
2023-12-13 08:13 | 0.0863
2023-12-13 08:14 | 0.0857
2023-12-13 08:15 | 0.0857
2023-12-13 08:16 | 0.0858
2023-12-13 08:17 | 0.086
2023-12-13 08:18 | 0.0861
2023-12-13 08:19 | 0.0863
2023-12-13 08:20 | 0.0859
2023-12-13 08:21 | 0.0861
2023-12-13 08:22 | 0.0861
2023-12-13 08:23 | 0.0862
2023-12-13 08:24 | 0.0857
2023-12-13 08:25 | 0.0857
2023-12-13 08:26 | 0.086
2023-12-13 08:27 | 0.0857
2023-12-13 08:28 | 0.0861
2023-12-13 08:29 | 0.0865
2023-12-13 08:30 | 0.0869
2023-12-13 08:31 | 0.0871
2023-12-13 08:32 | 0.0869
2023-12-13 08:33 | 0.0869
2023-12-13 08:34 | 0.0007
2023-12-13 08:35 | 0
2023-12-13 08:36 | 0
2023-12-13 08:37 | 0
2023-12-13 08:38 | 0
2023-12-13 08:39 | 0
2023-12-13 08:40 | 0.0934
2023-12-13 08:41 | 0.0858
2023-12-13 08:42 | 0.0862
2023-12-13 08:43 | 0.0865
2023-12-13 08:44 | 0.0864
2023-12-13 08:45 | 0.0863
2023-12-13 08:46 | 0.0866
2023-12-13 08:47 | 0.0859
2023-12-13 08:48 | 0.0861
2023-12-13 08:49 | 0.0866
2023-12-13 08:50 | 0.0866
2023-12-13 08:51 | 0.0867
2023-12-13 08:52 | 0.0869
2023-12-13 08:53 | 0.0867
2023-12-13 08:54 | 0.0862
2023-12-13 08:55 | 0.086
2023-12-13 08:56 | 0.0862
2023-12-13 08:57 | 0.0864
2023-12-13 08:58 | 0.0861
2023-12-13 08:59 | 0.0861
2023-12-13 09:00 | 0.0864
2023-12-13 09:01 | 0.0856
2023-12-13 09:02 | 0.0866
2023-12-13 09:03 | 0.0862
2023-12-13 09:04 | 0.0865
2023-12-13 09:05 | 0.0869
2023-12-13 09:06 | 0.0865
2023-12-13 09:07 | 0.0866
2023-12-13 09:08 | 0.0872
2023-12-13 09:09 | 0.0869
2023-12-13 09:10 | 0.0873
2023-12-13 09:11 | 0.0872
2023-12-13 09:12 | 0.0872
2023-12-13 09:13 | 0.0872
2023-12-13 09:14 | 0.0871
2023-12-13 09:15 | 0.0864
2023-12-13 09:16 | 0.0869
2023-12-13 09:17 | 0.0869
2023-12-13 09:18 | 0.0868
2023-12-13 09:19 | 0.087
2023-12-13 09:20 | 0.0865
2023-12-13 09:21 | 0.0866
2023-12-13 09:22 | 0.087
2023-12-13 09:23 | 0.0868
2023-12-13 09:24 | 0.087
2023-12-13 09:25 | 0.0866
2023-12-13 09:26 | 0.0871
2023-12-13 09:27 | 0.0873
2023-12-13 09:28 | 0.0871
2023-12-13 09:29 | 0.0871
2023-12-13 09:30 | 0.0868
2023-12-13 09:31 | 0.0864
2023-12-13 09:32 | 0.0866
2023-12-13 09:33 | 0.0866
2023-12-13 09:34 | 0.0147
2023-12-13 09:35 | 0
2023-12-13 09:36 | 0
2023-12-13 09:37 | 0
2023-12-13 09:38 | 0
2023-12-13 09:39 | 0
2023-12-13 09:40 | 0.0759
2023-12-13 09:41 | 0.0858
2023-12-13 09:42 | 0.0861
2023-12-13 09:43 | 0.0857
2023-12-13 09:44 | 0.0851
2023-12-13 09:45 | 0.0855
2023-12-13 09:46 | 0.0865
2023-12-13 09:47 | 0.0861
2023-12-13 09:48 | 0.0866
2023-12-13 09:49 | 0.0868
2023-12-13 09:50 | 0.0871
2023-12-13 09:51 | 0.0866
2023-12-13 09:52 | 0.0857
2023-12-13 09:53 | 0.0865
2023-12-13 09:54 | 0.0863
2023-12-13 09:55 | 0.0871
2023-12-13 09:56 | 0.0871
2023-12-13 09:57 | 0.0865
2023-12-13 09:58 | 0.0865
2023-12-13 09:59 | 0.0868
2023-12-13 10:00 | 0.0864
2023-12-13 10:01 | 0.0863
2023-12-13 10:02 | 0.087
2023-12-13 10:03 | 0.0872
2023-12-13 10:04 | 0.0872
2023-12-13 10:05 | 0.087
2023-12-13 10:06 | 0.0866
2023-12-13 10:07 | 0.0859
2023-12-13 10:08 | 0.0861
2023-12-13 10:09 | 0.0864
2023-12-13 10:10 | 0.0862
2023-12-13 10:11 | 0.0865
2023-12-13 10:12 | 0.0857
2023-12-13 10:13 | 0.0865
2023-12-13 10:14 | 0.0864
2023-12-13 10:15 | 0.0865
2023-12-13 10:16 | 0.086
2023-12-13 10:17 | 0.0856
2023-12-13 10:18 | 0.0868
2023-12-13 10:19 | 0.0872
2023-12-13 10:20 | 0.0867
2023-12-13 10:21 | 0.0865
2023-12-13 10:22 | 0.0868
2023-12-13 10:23 | 0.0867
2023-12-13 10:24 | 0.0867
2023-12-13 10:25 | 0.0873
2023-12-13 10:26 | 0.0868
2023-12-13 10:27 | 0.0863
2023-12-13 10:28 | 0.0873
2023-12-13 10:29 | 0.0879
2023-12-13 10:30 | 0.0877
2023-12-13 10:31 | 0.0874
2023-12-13 10:32 | 0.0872
2023-12-13 10:33 | 0.0868
2023-12-13 10:34 | 0.0415
2023-12-13 10:35 | 0
2023-12-13 10:36 | 0
2023-12-13 10:37 | 0
2023-12-13 10:38 | 0
2023-12-13 10:39 | 0
2023-12-13 10:40 | 0.0479
2023-12-13 10:41 | 0.0847
2023-12-13 10:42 | 0.0857
2023-12-13 10:43 | 0.0854
2023-12-13 10:44 | 0.0865
2023-12-13 10:45 | 0.0867
2023-12-13 10:46 | 0.0864
2023-12-13 10:47 | 0.0868
2023-12-13 10:48 | 0.0872
2023-12-13 10:49 | 0.087
2023-12-13 10:50 | 0.0862
2023-12-13 10:51 | 0.0862
2023-12-13 10:52 | 0.086
2023-12-13 10:53 | 0.0865
2023-12-13 10:54 | 0.0852
2023-12-13 10:55 | 0.0862
2023-12-13 10:56 | 0.0873
2023-12-13 10:57 | 0.0868
2023-12-13 10:58 | 0.0865
2023-12-13 10:59 | 0.0869
2023-12-13 11:00 | 0.0869
2023-12-13 11:01 | 0.0868
2023-12-13 11:02 | 0.0863
2023-12-13 11:03 | 0.0873
2023-12-13 11:04 | 0.0866
2023-12-13 11:05 | 0.0873
2023-12-13 11:06 | 0.0863
2023-12-13 11:07 | 0.0875
2023-12-13 11:08 | 0.0868
2023-12-13 11:09 | 0.0868
2023-12-13 11:10 | 0.0876
2023-12-13 11:11 | 0.0872
2023-12-13 11:12 | 0.087
2023-12-13 11:13 | 0.0872
2023-12-13 11:14 | 0.0861
2023-12-13 11:15 | 0.086
2023-12-13 11:16 | 0.0865
2023-12-13 11:17 | 0.0861
2023-12-13 11:18 | 0.0861
2023-12-13 11:19 | 0.0863
2023-12-13 11:20 | 0.0862
2023-12-13 11:21 | 0.0866
2023-12-13 11:22 | 0.0863
2023-12-13 11:23 | 0.0864
2023-12-13 11:24 | 0.0863
2023-12-13 11:25 | 0.0869
2023-12-13 11:26 | 0.0873
2023-12-13 11:27 | 0.087
2023-12-13 11:28 | 0.0875
2023-12-13 11:29 | 0.0871
2023-12-13 11:30 | 0.0866
2023-12-13 11:31 | 0.0869
2023-12-13 11:32 | 0.0867
2023-12-13 11:33 | 0.0869
2023-12-13 11:34 | 0.0712
2023-12-13 11:35 | 0
2023-12-13 11:36 | 0
2023-12-13 11:37 | 0
2023-12-13 11:38 | 0
2023-12-13 11:39 | 0
2023-12-13 11:40 | 0.0191
2023-12-13 11:41 | 0.0856
2023-12-13 11:42 | 0.0863
2023-12-13 11:43 | 0.0869
2023-12-13 11:44 | 0.0861
2023-12-13 11:45 | 0.086
2023-12-13 11:46 | 0.0857
2023-12-13 11:47 | 0.086
2023-12-13 11:48 | 0.0856
2023-12-13 11:49 | 0.0857
2023-12-13 11:50 | 0.0861
2023-12-13 11:51 | 0.0858
2023-12-13 11:52 | 0.0859
2023-12-13 11:53 | 0.0858
2023-12-13 11:54 | 0.0862
2023-12-13 11:55 | 0.0868
2023-12-13 11:56 | 0.0871
2023-12-13 11:57 | 0.0867
2023-12-13 11:58 | 0.087
2023-12-13 11:59 | 0.0871
2023-12-13 12:00 | 0.087
2023-12-13 12:01 | 0.0869
2023-12-13 12:02 | 0.0872
2023-12-13 12:03 | 0.087
2023-12-13 12:04 | 0.0864
2023-12-13 12:05 | 0.0871
2023-12-13 12:06 | 0.087
2023-12-13 12:07 | 0.0872
2023-12-13 12:08 | 0.0873
2023-12-13 12:09 | 0.0865
2023-12-13 12:10 | 0.0871
2023-12-13 12:11 | 0.0874
2023-12-13 12:12 | 0.0871
2023-12-13 12:13 | 0.0869
2023-12-13 12:14 | 0.0867
2023-12-13 12:15 | 0.087
2023-12-13 12:16 | 0.087
2023-12-13 12:17 | 0.0874
2023-12-13 12:18 | 0.0875
2023-12-13 12:19 | 0.0873
2023-12-13 12:20 | 0.0869
2023-12-13 12:21 | 0.0867
2023-12-13 12:22 | 0.086
2023-12-13 12:23 | 0.0862
2023-12-13 12:24 | 0.087
2023-12-13 12:25 | 0.0872
2023-12-13 12:26 | 0.0873
2023-12-13 12:27 | 0.0875
2023-12-13 12:28 | 0.087
2023-12-13 12:29 | 0.0872
2023-12-13 12:30 | 0.0877
2023-12-13 12:31 | 0.0875
2023-12-13 12:32 | 0.0869
2023-12-13 12:33 | 0.0871
2023-12-13 12:34 | 0.0865
2023-12-13 12:35 | 0.0111
2023-12-13 12:36 | 0
2023-12-13 12:37 | 0
2023-12-13 12:38 | 0
2023-12-13 12:39 | 0
2023-12-13 12:40 | 0
2023-12-13 12:41 | 0.0797
2023-12-13 12:42 | 0.0872
2023-12-13 12:43 | 0.0871
2023-12-13 12:44 | 0.0871
2023-12-13 12:45 | 0.0869
2023-12-13 12:46 | 0.087
2023-12-13 12:47 | 0.0865
2023-12-13 12:48 | 0.0864
2023-12-13 12:49 | 0.0864
2023-12-13 12:50 | 0.0857
2023-12-13 12:51 | 0.0862
2023-12-13 12:52 | 0.0864
2023-12-13 12:53 | 0.0867
2023-12-13 12:54 | 0.0866
2023-12-13 12:55 | 0.0867
2023-12-13 12:56 | 0.0868
2023-12-13 12:57 | 0.0862
2023-12-13 12:58 | 0.0859
2023-12-13 12:59 | 0.0871
2023-12-13 13:00 | 0.0874
2023-12-13 13:01 | 0.0871
2023-12-13 13:02 | 0.0874
2023-12-13 13:03 | 0.0874
2023-12-13 13:04 | 0.0869
2023-12-13 13:05 | 0.0868
2023-12-13 13:06 | 0.0868
2023-12-13 13:07 | 0.0869
2023-12-13 13:08 | 0.0862
2023-12-13 13:09 | 0.0869
2023-12-13 13:10 | 0.0866
2023-12-13 13:11 | 0.0868
2023-12-13 13:12 | 0.0861
2023-12-13 13:13 | 0.0864
2023-12-13 13:14 | 0.087
2023-12-13 13:15 | 0.0871
2023-12-13 13:16 | 0.0872
2023-12-13 13:17 | 0.0873
2023-12-13 13:18 | 0.0874
2023-12-13 13:19 | 0.0872
2023-12-13 13:20 | 0.0876
2023-12-13 13:21 | 0.0871
2023-12-13 13:22 | 0.0875
2023-12-13 13:23 | 0.0876
2023-12-13 13:24 | 0.0873
2023-12-13 13:25 | 0.0877
2023-12-13 13:26 | 0.0879
2023-12-13 13:27 | 0.0876
2023-12-13 13:28 | 0.087
2023-12-13 13:29 | 0.0872
2023-12-13 13:30 | 0.0873
2023-12-13 13:31 | 0.0874
2023-12-13 13:32 | 0.087
2023-12-13 13:33 | 0.0869
2023-12-13 13:34 | 0.0871
2023-12-13 13:35 | 0.0358
2023-12-13 13:36 | 0
2023-12-13 13:37 | 0
2023-12-13 13:38 | 0
2023-12-13 13:39 | 0
2023-12-13 13:40 | 0
2023-12-13 13:41 | 0.0545
2023-12-13 13:42 | 0.0872
2023-12-13 13:43 | 0.0869
2023-12-13 13:44 | 0.0871
2023-12-13 13:45 | 0.087
2023-12-13 13:46 | 0.087
2023-12-13 13:47 | 0.0872
2023-12-13 13:48 | 0.0872
2023-12-13 13:49 | 0.0873
2023-12-13 13:50 | 0.0868
2023-12-13 13:51 | 0.0868
2023-12-13 13:52 | 0.0863
2023-12-13 13:53 | 0.0768
2023-12-13 13:54 | 0
2023-12-13 13:55 | 0
2023-12-13 13:56 | 0
2023-12-13 13:57 | 0
2023-12-13 13:58 | 0
2023-12-13 13:59 | 0
2023-12-13 14:00 | 0
2023-12-13 14:01 | 0
2023-12-13 14:02 | 0
2023-12-13 14:03 | 0
2023-12-13 14:04 | 0
2023-12-13 14:05 | 0
2023-12-13 14:06 | 0
2023-12-13 14:07 | 0
2023-12-13 14:08 | 0
2023-12-13 14:09 | 0
2023-12-13 14:10 | 0
2023-12-13 14:11 | 0
2023-12-13 14:12 | 0
2023-12-13 14:13 | 0
2023-12-13 14:14 | 0
2023-12-13 14:15 | 0
2023-12-13 14:16 | 0
2023-12-13 14:17 | 0
2023-12-13 14:18 | 0
2023-12-13 14:19 | 0
2023-12-13 14:20 | 0
2023-12-13 14:21 | 0
2023-12-13 14:22 | 0
2023-12-13 14:23 | 0
2023-12-13 14:24 | 0
2023-12-13 14:25 | 0
2023-12-13 14:26 | 0
2023-12-13 14:27 | 0
2023-12-13 14:28 | 0
2023-12-13 14:29 | 0
2023-12-13 14:30 | 0
2023-12-13 14:31 | 0
2023-12-13 14:32 | 0
2023-12-13 14:33 | 0
2023-12-13 14:34 | 0
2023-12-13 14:35 | 0
2023-12-13 14:36 | 0
2023-12-13 14:37 | 0
2023-12-13 14:38 | 0
2023-12-13 14:39 | 0
2023-12-13 14:40 | 0
2023-12-13 14:41 | 0
2023-12-13 14:42 | 0.0821
2023-12-13 14:43 | 0.0859
2023-12-13 14:44 | 0.0853
2023-12-13 14:45 | 0.0854
2023-12-13 14:46 | 0.0862
2023-12-13 14:47 | 0.0861
2023-12-13 14:48 | 0.0862
2023-12-13 14:49 | 0.0864
2023-12-13 14:50 | 0.0867
2023-12-13 14:51 | 0.087
2023-12-13 14:52 | 0.0869
2023-12-13 14:53 | 0.0867
2023-12-13 14:54 | 0.0148
2023-12-13 14:55 | 0
2023-12-13 14:56 | 0
2023-12-13 14:57 | 0
2023-12-13 14:58 | 0
2023-12-13 14:59 | 0
2023-12-13 15:00 | 0
2023-12-13 15:01 | 0
2023-12-13 15:02 | 0
2023-12-13 15:03 | 0
2023-12-13 15:04 | 0
2023-12-13 15:05 | 0
2023-12-13 15:06 | 0
2023-12-13 15:07 | 0
2023-12-13 15:08 | 0
2023-12-13 15:09 | 0
2023-12-13 15:10 | 0
2023-12-13 15:11 | 0
2023-12-13 15:12 | 0
2023-12-13 15:13 | 0
2023-12-13 15:14 | 0
2023-12-13 15:15 | 0
2023-12-13 15:16 | 0
2023-12-13 15:17 | 0
2023-12-13 15:18 | 0
2023-12-13 15:19 | 0
2023-12-13 15:20 | 0
2023-12-13 15:21 | 0
2023-12-13 15:22 | 0
2023-12-13 15:23 | 0
2023-12-13 15:24 | 0
2023-12-13 15:25 | 0
2023-12-13 15:26 | 0
2023-12-13 15:27 | 0
2023-12-13 15:28 | 0
2023-12-13 15:29 | 0
2023-12-13 15:30 | 0
2023-12-13 15:31 | 0
2023-12-13 15:32 | 0
2023-12-13 15:33 | 0
2023-12-13 15:34 | 0
2023-12-13 15:35 | 0
2023-12-13 15:36 | 0
2023-12-13 15:37 | 0
2023-12-13 15:38 | 0
2023-12-13 15:39 | 0
2023-12-13 15:40 | 0
2023-12-13 15:41 | 0
2023-12-13 15:42 | 0.0627
2023-12-13 15:43 | 0.0857
2023-12-13 15:44 | 0.0862
2023-12-13 15:45 | 0.086
2023-12-13 15:46 | 0.0861
2023-12-13 15:47 | 0.0861
2023-12-13 15:48 | 0.0854
2023-12-13 15:49 | 0.0854
2023-12-13 15:50 | 0.086
2023-12-13 15:51 | 0.0863
2023-12-13 15:52 | 0.0864
2023-12-13 15:53 | 0.086
2023-12-13 15:54 | 0.0334
2023-12-13 15:55 | 0
2023-12-13 15:56 | 0
2023-12-13 15:57 | 0
2023-12-13 15:58 | 0
2023-12-13 15:59 | 0
2023-12-13 16:00 | 0
2023-12-13 16:01 | 0
2023-12-13 16:02 | 0
2023-12-13 16:03 | 0
2023-12-13 16:04 | 0
2023-12-13 16:05 | 0
2023-12-13 16:06 | 0
2023-12-13 16:07 | 0
2023-12-13 16:08 | 0
2023-12-13 16:09 | 0
2023-12-13 16:10 | 0
2023-12-13 16:11 | 0
2023-12-13 16:12 | 0
2023-12-13 16:13 | 0
2023-12-13 16:14 | 0
2023-12-13 16:15 | 0
2023-12-13 16:16 | 0
2023-12-13 16:17 | 0
2023-12-13 16:18 | 0
2023-12-13 16:19 | 0
2023-12-13 16:20 | 0
2023-12-13 16:21 | 0
2023-12-13 16:22 | 0
2023-12-13 16:23 | 0
2023-12-13 16:24 | 0
2023-12-13 16:25 | 0
2023-12-13 16:26 | 0
2023-12-13 16:27 | 0
2023-12-13 16:28 | 0
2023-12-13 16:29 | 0
2023-12-13 16:30 | 0
2023-12-13 16:31 | 0
2023-12-13 16:32 | 0
2023-12-13 16:33 | 0
2023-12-13 16:34 | 0
2023-12-13 16:35 | 0
2023-12-13 16:36 | 0
2023-12-13 16:37 | 0
2023-12-13 16:38 | 0
2023-12-13 16:39 | 0
2023-12-13 16:40 | 0
2023-12-13 16:41 | 0
2023-12-13 16:42 | 0.0446
2023-12-13 16:43 | 0.0859
2023-12-13 16:44 | 0.0864
2023-12-13 16:45 | 0.0863
2023-12-13 16:46 | 0.0863
2023-12-13 16:47 | 0.0861
2023-12-13 16:48 | 0.0858
2023-12-13 16:49 | 0.0856
2023-12-13 16:50 | 0.0861
2023-12-13 16:51 | 0.0856
2023-12-13 16:52 | 0.0855
2023-12-13 16:53 | 0.0863
2023-12-13 16:54 | 0.0539
2023-12-13 16:55 | 0
2023-12-13 16:56 | 0
2023-12-13 16:57 | 0
2023-12-13 16:58 | 0
2023-12-13 16:59 | 0
2023-12-13 17:00 | 0
2023-12-13 17:01 | 0
2023-12-13 17:02 | 0
2023-12-13 17:03 | 0
2023-12-13 17:04 | 0
2023-12-13 17:05 | 0
2023-12-13 17:06 | 0
2023-12-13 17:07 | 0
2023-12-13 17:08 | 0
2023-12-13 17:09 | 0
2023-12-13 17:10 | 0
2023-12-13 17:11 | 0
2023-12-13 17:12 | 0
2023-12-13 17:13 | 0
2023-12-13 17:14 | 0
2023-12-13 17:15 | 0
2023-12-13 17:16 | 0
2023-12-13 17:17 | 0
2023-12-13 17:18 | 0
2023-12-13 17:19 | 0
2023-12-13 17:20 | 0
2023-12-13 17:21 | 0
2023-12-13 17:22 | 0
2023-12-13 17:23 | 0
2023-12-13 17:24 | 0
2023-12-13 17:25 | 0
2023-12-13 17:26 | 0
2023-12-13 17:27 | 0
2023-12-13 17:28 | 0
2023-12-13 17:29 | 0
2023-12-13 17:30 | 0
2023-12-13 17:31 | 0
2023-12-13 17:32 | 0
2023-12-13 17:33 | 0
2023-12-13 17:34 | 0
2023-12-13 17:35 | 0
2023-12-13 17:36 | 0
2023-12-13 17:37 | 0
2023-12-13 17:38 | 0
2023-12-13 17:39 | 0
2023-12-13 17:40 | 0
2023-12-13 17:41 | 0
2023-12-13 17:42 | 0.0192
2023-12-13 17:43 | 0.0841
2023-12-13 17:44 | 0.0847
2023-12-13 17:45 | 0.0847
2023-12-13 17:46 | 0.0854
2023-12-13 17:47 | 0.0857
2023-12-13 17:48 | 0.0859
2023-12-13 17:49 | 0.0861
2023-12-13 17:50 | 0.0863
2023-12-13 17:51 | 0.0863
2023-12-13 17:52 | 0.0859
2023-12-13 17:53 | 0.0858
2023-12-13 17:54 | 0.0777
2023-12-13 17:55 | 0
2023-12-13 17:56 | 0
2023-12-13 17:57 | 0
2023-12-13 17:58 | 0
2023-12-13 17:59 | 0
2023-12-13 18:00 | 0
2023-12-13 18:01 | 0
2023-12-13 18:02 | 0
2023-12-13 18:03 | 0
2023-12-13 18:04 | 0
2023-12-13 18:05 | 0
2023-12-13 18:06 | 0
2023-12-13 18:07 | 0
2023-12-13 18:08 | 0
2023-12-13 18:09 | 0
2023-12-13 18:10 | 0
2023-12-13 18:11 | 0
2023-12-13 18:12 | 0
2023-12-13 18:13 | 0
2023-12-13 18:14 | 0
2023-12-13 18:15 | 0
2023-12-13 18:16 | 0
2023-12-13 18:17 | 0
2023-12-13 18:18 | 0
2023-12-13 18:19 | 0
2023-12-13 18:20 | 0
2023-12-13 18:21 | 0
2023-12-13 18:22 | 0
2023-12-13 18:23 | 0
2023-12-13 18:24 | 0
2023-12-13 18:25 | 0
2023-12-13 18:26 | 0
2023-12-13 18:27 | 0
2023-12-13 18:28 | 0
2023-12-13 18:29 | 0
2023-12-13 18:30 | 0
2023-12-13 18:31 | 0
2023-12-13 18:32 | 0
2023-12-13 18:33 | 0
2023-12-13 18:34 | 0
2023-12-13 18:35 | 0
2023-12-13 18:36 | 0
2023-12-13 18:37 | 0
2023-12-13 18:38 | 0
2023-12-13 18:39 | 0
2023-12-13 18:40 | 0
2023-12-13 18:41 | 0
2023-12-13 18:42 | 0
2023-12-13 18:43 | 0.078
2023-12-13 18:44 | 0.0856
2023-12-13 18:45 | 0.0858
2023-12-13 18:46 | 0.086
2023-12-13 18:47 | 0.0863
2023-12-13 18:48 | 0.0865
2023-12-13 18:49 | 0.0866
2023-12-13 18:50 | 0.0864
2023-12-13 18:51 | 0.0859
2023-12-13 18:52 | 0.0858
2023-12-13 18:53 | 0.0859
2023-12-13 18:54 | 0.086
2023-12-13 18:55 | 0.02
2023-12-13 18:56 | 0
2023-12-13 18:57 | 0
2023-12-13 18:58 | 0
2023-12-13 18:59 | 0
2023-12-13 19:00 | 0
2023-12-13 19:01 | 0
2023-12-13 19:02 | 0
2023-12-13 19:03 | 0
2023-12-13 19:04 | 0
2023-12-13 19:05 | 0
2023-12-13 19:06 | 0
2023-12-13 19:07 | 0
2023-12-13 19:08 | 0
2023-12-13 19:09 | 0
2023-12-13 19:10 | 0
2023-12-13 19:11 | 0
2023-12-13 19:12 | 0
2023-12-13 19:13 | 0
2023-12-13 19:14 | 0
2023-12-13 19:15 | 0
2023-12-13 19:16 | 0
2023-12-13 19:17 | 0
2023-12-13 19:18 | 0
2023-12-13 19:19 | 0
2023-12-13 19:20 | 0
2023-12-13 19:21 | 0
2023-12-13 19:22 | 0
2023-12-13 19:23 | 0
2023-12-13 19:24 | 0
2023-12-13 19:25 | 0
2023-12-13 19:26 | 0
2023-12-13 19:27 | 0
2023-12-13 19:28 | 0
2023-12-13 19:29 | 0
2023-12-13 19:30 | 0
2023-12-13 19:31 | 0
2023-12-13 19:32 | 0
2023-12-13 19:33 | 0
2023-12-13 19:34 | 0
2023-12-13 19:35 | 0
2023-12-13 19:36 | 0
2023-12-13 19:37 | 0
2023-12-13 19:38 | 0
2023-12-13 19:39 | 0
2023-12-13 19:40 | 0
2023-12-13 19:41 | 0
2023-12-13 19:42 | 0
2023-12-13 19:43 | 0.0504
2023-12-13 19:44 | 0.0855
2023-12-13 19:45 | 0.0861
2023-12-13 19:46 | 0.086
2023-12-13 19:47 | 0.0861
2023-12-13 19:48 | 0.086
2023-12-13 19:49 | 0.0865
2023-12-13 19:50 | 0.0864
2023-12-13 19:51 | 0.0862
2023-12-13 19:52 | 0.0864
2023-12-13 19:53 | 0.0865
2023-12-13 19:54 | 0.0867
2023-12-13 19:55 | 0.048
2023-12-13 19:56 | 0
2023-12-13 19:57 | 0
2023-12-13 19:58 | 0
2023-12-13 19:59 | 0
2023-12-13 20:00 | 0
2023-12-13 20:01 | 0
2023-12-13 20:02 | 0
2023-12-13 20:03 | 0
2023-12-13 20:04 | 0
2023-12-13 20:05 | 0
2023-12-13 20:06 | 0
2023-12-13 20:07 | 0
2023-12-13 20:08 | 0
2023-12-13 20:09 | 0
2023-12-13 20:10 | 0
2023-12-13 20:11 | 0.0295
2023-12-13 20:12 | 0.0858
2023-12-13 20:13 | 0.0867
2023-12-13 20:14 | 0.0868
2023-12-13 20:15 | 0.0866
2023-12-13 20:16 | 0.0864
2023-12-13 20:17 | 0.0866
2023-12-13 20:18 | 0.0859
2023-12-13 20:19 | 0.0855
2023-12-13 20:20 | 0.0866
2023-12-13 20:21 | 0.0858
2023-12-13 20:22 | 0.0866
2023-12-13 20:23 | 0.0863
2023-12-13 20:24 | 0.0867
2023-12-13 20:25 | 0.0875
2023-12-13 20:26 | 0.0867
2023-12-13 20:27 | 0.0865
2023-12-13 20:28 | 0.0873
2023-12-13 20:29 | 0.0871
2023-12-13 20:30 | 0.087
2023-12-13 20:31 | 0.0868
2023-12-13 20:32 | 0.0867
2023-12-13 20:33 | 0.0873
2023-12-13 20:34 | 0.0876
2023-12-13 20:35 | 0.0876
2023-12-13 20:36 | 0.087
2023-12-13 20:37 | 0.0872
2023-12-13 20:38 | 0.0869
2023-12-13 20:39 | 0.0868
2023-12-13 20:40 | 0.0868
2023-12-13 20:41 | 0.0876
2023-12-13 20:42 | 0.0874
2023-12-13 20:43 | 0.0871
2023-12-13 20:44 | 0.0874
2023-12-13 20:45 | 0.0871
2023-12-13 20:46 | 0.0865
2023-12-13 20:47 | 0.0866
2023-12-13 20:48 | 0.0868
2023-12-13 20:49 | 0.0872
2023-12-13 20:50 | 0.0871
2023-12-13 20:51 | 0.0872
2023-12-13 20:52 | 0.087
2023-12-13 20:53 | 0.0873
2023-12-13 20:54 | 0.0875
2023-12-13 20:55 | 0.0876
2023-12-13 20:56 | 0.0879
2023-12-13 20:57 | 0.0877
2023-12-13 20:58 | 0.0875
2023-12-13 20:59 | 0.087
2023-12-13 21:00 | 0.0874
2023-12-13 21:01 | 0.0873
2023-12-13 21:02 | 0.0875
2023-12-13 21:03 | 0.0874
2023-12-13 21:04 | 0.0871
2023-12-13 21:05 | 0.0875
2023-12-13 21:06 | 0.008
2023-12-13 21:07 | 0
2023-12-13 21:08 | 0
2023-12-13 21:09 | 0
2023-12-13 21:10 | 0
2023-12-13 21:11 | 0
2023-12-13 21:12 | 0.082
2023-12-13 21:13 | 0.087
2023-12-13 21:14 | 0.0868
2023-12-13 21:15 | 0.087
2023-12-13 21:16 | 0.0868
2023-12-13 21:17 | 0.0871
2023-12-13 21:18 | 0.0868
2023-12-13 21:19 | 0.0872
2023-12-13 21:20 | 0.0872
2023-12-13 21:21 | 0.0875
2023-12-13 21:22 | 0.0871
2023-12-13 21:23 | 0.0874
2023-12-13 21:24 | 0.0877
2023-12-13 21:25 | 0.0874
2023-12-13 21:26 | 0.0868
2023-12-13 21:27 | 0.0875
2023-12-13 21:28 | 0.087
2023-12-13 21:29 | 0.0873
2023-12-13 21:30 | 0.0872
2023-12-13 21:31 | 0.0874
2023-12-13 21:32 | 0.0873
2023-12-13 21:33 | 0.0874
2023-12-13 21:34 | 0.0875
2023-12-13 21:35 | 0.0878
2023-12-13 21:36 | 0.0872
2023-12-13 21:37 | 0.0872
2023-12-13 21:38 | 0.0873
2023-12-13 21:39 | 0.0877
2023-12-13 21:40 | 0.0877
2023-12-13 21:41 | 0.0877
2023-12-13 21:42 | 0.0879
2023-12-13 21:43 | 0.0876
2023-12-13 21:44 | 0.0876
2023-12-13 21:45 | 0.0875
2023-12-13 21:46 | 0.0876
2023-12-13 21:47 | 0.0873
2023-12-13 21:48 | 0.0877
2023-12-13 21:49 | 0.0874
2023-12-13 21:50 | 0.0878
2023-12-13 21:51 | 0.0875
2023-12-13 21:52 | 0.0875
2023-12-13 21:53 | 0.0873
2023-12-13 21:54 | 0.0875
2023-12-13 21:55 | 0.0874
2023-12-13 21:56 | 0.0878
2023-12-13 21:57 | 0.0876
2023-12-13 21:58 | 0.0875
2023-12-13 21:59 | 0.0877
2023-12-13 22:00 | 0.0881
2023-12-13 22:01 | 0.0877
2023-12-13 22:02 | 0.0874
2023-12-13 22:03 | 0.0876
2023-12-13 22:04 | 0.0877
2023-12-13 22:05 | 0.0884
2023-12-13 22:06 | 0.035
2023-12-13 22:07 | 0
2023-12-13 22:08 | 0
2023-12-13 22:09 | 0
2023-12-13 22:10 | 0
2023-12-13 22:11 | 0
2023-12-13 22:12 | 0.0574
2023-12-13 22:13 | 0.0875
2023-12-13 22:14 | 0.0875
2023-12-13 22:15 | 0.0872
2023-12-13 22:16 | 0.0876
2023-12-13 22:17 | 0.0875
2023-12-13 22:18 | 0.0878
2023-12-13 22:19 | 0.0878
2023-12-13 22:20 | 0.0881
2023-12-13 22:21 | 0.0875
2023-12-13 22:22 | 0.0877
2023-12-13 22:23 | 0.0872
2023-12-13 22:24 | 0.088
2023-12-13 22:25 | 0.088
2023-12-13 22:26 | 0.0879
2023-12-13 22:27 | 0.0876
2023-12-13 22:28 | 0.088
2023-12-13 22:29 | 0.0882
2023-12-13 22:30 | 0.0884
2023-12-13 22:31 | 0.088
2023-12-13 22:32 | 0.0881
2023-12-13 22:33 | 0.0877
2023-12-13 22:34 | 0.0884
2023-12-13 22:35 | 0.0885
2023-12-13 22:36 | 0.0884
2023-12-13 22:37 | 0.0878
2023-12-13 22:38 | 0.0885
2023-12-13 22:39 | 0.0885
2023-12-13 22:40 | 0.0879
2023-12-13 22:41 | 0.0881
2023-12-13 22:42 | 0.0883
2023-12-13 22:43 | 0.0882
2023-12-13 22:44 | 0.0885
2023-12-13 22:45 | 0.0886
2023-12-13 22:46 | 0.0886
2023-12-13 22:47 | 0.0884
2023-12-13 22:48 | 0.0888
2023-12-13 22:49 | 0.0885
2023-12-13 22:50 | 0.0887
2023-12-13 22:51 | 0.0885
2023-12-13 22:52 | 0.0885
2023-12-13 22:53 | 0.0886
2023-12-13 22:54 | 0.0887
2023-12-13 22:55 | 0.0884
2023-12-13 22:56 | 0.0883
2023-12-13 22:57 | 0.0885
2023-12-13 22:58 | 0.0887
2023-12-13 22:59 | 0.0883
2023-12-13 23:00 | 0.0884
2023-12-13 23:01 | 0.0884
2023-12-13 23:02 | 0.0886
2023-12-13 23:03 | 0.088
2023-12-13 23:04 | 0.088
2023-12-13 23:05 | 0.0883
2023-12-13 23:06 | 0.0574
2023-12-13 23:07 | 0
2023-12-13 23:08 | 0
2023-12-13 23:09 | 0
2023-12-13 23:10 | 0
2023-12-13 23:11 | 0
2023-12-13 23:12 | 0.0351
2023-12-13 23:13 | 0.0879
2023-12-13 23:14 | 0.0883
2023-12-13 23:15 | 0.0885
2023-12-13 23:16 | 0.0883
2023-12-13 23:17 | 0.0886
2023-12-13 23:18 | 0.0884
2023-12-13 23:19 | 0.0885
2023-12-13 23:20 | 0.0884
2023-12-13 23:21 | 0.0883
2023-12-13 23:22 | 0.0884
2023-12-13 23:23 | 0.0882
2023-12-13 23:24 | 0.0885
2023-12-13 23:25 | 0.0883
2023-12-13 23:26 | 0.0884
2023-12-13 23:27 | 0.0884
2023-12-13 23:28 | 0.0882
2023-12-13 23:29 | 0.0884
2023-12-13 23:30 | 0.0884
2023-12-13 23:31 | 0.0883
2023-12-13 23:32 | 0.0887
2023-12-13 23:33 | 0.0886
2023-12-13 23:34 | 0.0887
2023-12-13 23:35 | 0.0887
2023-12-13 23:36 | 0.0886
2023-12-13 23:37 | 0.0888
2023-12-13 23:38 | 0.0885
2023-12-13 23:39 | 0.0889
2023-12-13 23:40 | 0.0886
2023-12-13 23:41 | 0.089
2023-12-13 23:42 | 0.0884
2023-12-13 23:43 | 0.0886
2023-12-13 23:44 | 0.0889
2023-12-13 23:45 | 0.088
2023-12-13 23:46 | 0.0879
2023-12-13 23:47 | 0.0881
2023-12-13 23:48 | 0.0877
2023-12-13 23:49 | 0.0881
2023-12-13 23:50 | 0.0884
2023-12-13 23:51 | 0.0882
2023-12-13 23:52 | 0.0879
2023-12-13 23:53 | 0.0879
2023-12-13 23:54 | 0.0879
2023-12-13 23:55 | 0.0882
2023-12-13 23:56 | 0.0879
2023-12-13 23:57 | 0.088
2023-12-13 23:58 | 0.0884
2023-12-13 23:59 | 0.0881
2023-12-14 | 0.0878
2023-12-14 00:01 | 0.088
2023-12-14 00:02 | 0.0882
2023-12-14 00:03 | 0.0878
2023-12-14 00:04 | 0.0882
2023-12-14 00:05 | 0.0881
2023-12-14 00:06 | 0.0748
2023-12-14 00:07 | 0
2023-12-14 00:08 | 0
2023-12-14 00:09 | 0
2023-12-14 00:10 | 0
2023-12-14 00:11 | 0
2023-12-14 00:12 | 0.0178
2023-12-14 00:13 | 0.0872
2023-12-14 00:14 | 0.0876
2023-12-14 00:15 | 0.0877
2023-12-14 00:16 | 0.0876
2023-12-14 00:17 | 0.0874
2023-12-14 00:18 | 0.0871
2023-12-14 00:19 | 0.0877
2023-12-14 00:20 | 0.0879
2023-12-14 00:21 | 0.0877
2023-12-14 00:22 | 0.0878
2023-12-14 00:23 | 0.0876
2023-12-14 00:24 | 0.0879
2023-12-14 00:25 | 0.0878
2023-12-14 00:26 | 0.088
2023-12-14 00:27 | 0.0881
2023-12-14 00:28 | 0.0881
2023-12-14 00:29 | 0.0878
2023-12-14 00:30 | 0.0878
2023-12-14 00:31 | 0.0879
2023-12-14 00:32 | 0.0877
2023-12-14 00:33 | 0.0881
2023-12-14 00:34 | 0.088
2023-12-14 00:35 | 0.0877
2023-12-14 00:36 | 0.088
2023-12-14 00:37 | 0.0876
2023-12-14 00:38 | 0.088
2023-12-14 00:39 | 0.088
2023-12-14 00:40 | 0.0881
2023-12-14 00:41 | 0.0882
2023-12-14 00:42 | 0.0881
2023-12-14 00:43 | 0.0883
2023-12-14 00:44 | 0.0883
2023-12-14 00:45 | 0.0882
2023-12-14 00:46 | 0.0881
2023-12-14 00:47 | 0.0882
2023-12-14 00:48 | 0.0883
2023-12-14 00:49 | 0.0884
2023-12-14 00:50 | 0.0885
2023-12-14 00:51 | 0.0886
2023-12-14 00:52 | 0.0886
2023-12-14 00:53 | 0.0885
2023-12-14 00:54 | 0.0884
2023-12-14 00:55 | 0.0884
2023-12-14 00:56 | 0.0877
2023-12-14 00:57 | 0.0879
2023-12-14 00:58 | 0.0878
2023-12-14 00:59 | 0.0878
2023-12-14 01:00 | 0.0883
2023-12-14 01:01 | 0.0883
2023-12-14 01:02 | 0.0882
2023-12-14 01:03 | 0.0883
2023-12-14 01:04 | 0.0883
2023-12-14 01:05 | 0.0883
2023-12-14 01:06 | 0.0868
2023-12-14 01:07 | 0
2023-12-14 01:08 | 0
2023-12-14 01:09 | 0
2023-12-14 01:10 | 0
2023-12-14 01:11 | 0
2023-12-14 01:12 | 0.0033
2023-12-14 01:13 | 0.0911
2023-12-14 01:14 | 0.0882
2023-12-14 01:15 | 0.0884
2023-12-14 01:16 | 0.0885
2023-12-14 01:17 | 0.0883
2023-12-14 01:18 | 0.0884
2023-12-14 01:19 | 0.0884
2023-12-14 01:20 | 0.0883
2023-12-14 01:21 | 0.0881
2023-12-14 01:22 | 0.0883
2023-12-14 01:23 | 0.0884
2023-12-14 01:24 | 0.0881
2023-12-14 01:25 | 0.0882
2023-12-14 01:26 | 0.0882
2023-12-14 01:27 | 0.0883
2023-12-14 01:28 | 0.0884
2023-12-14 01:29 | 0.0885
2023-12-14 01:30 | 0.0884
2023-12-14 01:31 | 0.0884
2023-12-14 01:32 | 0.0885
2023-12-14 01:33 | 0.0885
2023-12-14 01:34 | 0.0883
2023-12-14 01:35 | 0.0883
2023-12-14 01:36 | 0.0882
2023-12-14 01:37 | 0.0883
2023-12-14 01:38 | 0.0882
2023-12-14 01:39 | 0.0882
2023-12-14 01:40 | 0.0883
2023-12-14 01:41 | 0.0885
2023-12-14 01:42 | 0.0884
2023-12-14 01:43 | 0.0884
2023-12-14 01:44 | 0.0884
2023-12-14 01:45 | 0.0883
2023-12-14 01:46 | 0.0884
2023-12-14 01:47 | 0.0884
2023-12-14 01:48 | 0.0884
2023-12-14 01:49 | 0.0885
2023-12-14 01:50 | 0.0884
2023-12-14 01:51 | 0.0885
2023-12-14 01:52 | 0.0884
2023-12-14 01:53 | 0.0885
2023-12-14 01:54 | 0.0884
2023-12-14 01:55 | 0.0884
2023-12-14 01:56 | 0.0885
2023-12-14 01:57 | 0.0885
2023-12-14 01:58 | 0.0885
2023-12-14 01:59 | 0.0884
2023-12-14 02:00 | 0.0887
2023-12-14 02:01 | 0.0884
2023-12-14 02:02 | 0.0885
2023-12-14 02:03 | 0.0884
2023-12-14 02:04 | 0.0887
2023-12-14 02:05 | 0.0889
2023-12-14 02:06 | 0.0886
2023-12-14 02:07 | 0.007
2023-12-14 02:08 | 0
2023-12-14 02:09 | 0
2023-12-14 02:10 | 0
2023-12-14 02:11 | 0
2023-12-14 02:12 | 0
2023-12-14 02:13 | 0.0868
2023-12-14 02:14 | 0.0884
2023-12-14 02:15 | 0.0883
2023-12-14 02:16 | 0.0882
2023-12-14 02:17 | 0.0883
2023-12-14 02:18 | 0.0883
2023-12-14 02:19 | 0.0882
2023-12-14 02:20 | 0.0885
2023-12-14 02:21 | 0.0887
2023-12-14 02:22 | 0.0884
2023-12-14 02:23 | 0.0885
2023-12-14 02:24 | 0.0886
2023-12-14 02:25 | 0.0886
2023-12-14 02:26 | 0.0887
2023-12-14 02:27 | 0.0888
2023-12-14 02:28 | 0.0887
2023-12-14 02:29 | 0.0886
2023-12-14 02:30 | 0.0885
2023-12-14 02:31 | 0.0884
2023-12-14 02:32 | 0.0883
2023-12-14 02:33 | 0.0884
2023-12-14 02:34 | 0.0884
2023-12-14 02:35 | 0.0882
2023-12-14 02:36 | 0.0886
2023-12-14 02:37 | 0.0885
2023-12-14 02:38 | 0.0885
2023-12-14 02:39 | 0.0885
2023-12-14 02:40 | 0.0884
2023-12-14 02:41 | 0.0885
2023-12-14 02:42 | 0.0882
2023-12-14 02:43 | 0.0883
2023-12-14 02:44 | 0.0884
2023-12-14 02:45 | 0.0882
2023-12-14 02:46 | 0.0885
2023-12-14 02:47 | 0.0886
2023-12-14 02:48 | 0.0884
2023-12-14 02:49 | 0.0885
2023-12-14 02:50 | 0.0886
2023-12-14 02:51 | 0.0887
2023-12-14 02:52 | 0.0887
2023-12-14 02:53 | 0.0889
2023-12-14 02:54 | 0.0886
2023-12-14 02:55 | 0.0887
2023-12-14 02:56 | 0.0886
2023-12-14 02:57 | 0.0887
2023-12-14 02:58 | 0.0886
2023-12-14 02:59 | 0.0885
2023-12-14 03:00 | 0.0885
2023-12-14 03:01 | 0.088
2023-12-14 03:02 | 0.0881
2023-12-14 03:03 | 0.0885
2023-12-14 03:04 | 0.0885
2023-12-14 03:05 | 0.0883
2023-12-14 03:06 | 0.0883
2023-12-14 03:07 | 0.0115
2023-12-14 03:08 | 0
2023-12-14 03:09 | 0
2023-12-14 03:10 | 0
2023-12-14 03:11 | 0
2023-12-14 03:12 | 0
2023-12-14 03:13 | 0.0827
2023-12-14 03:14 | 0.088
2023-12-14 03:15 | 0.0884
2023-12-14 03:16 | 0.0885
2023-12-14 03:17 | 0.0883
2023-12-14 03:18 | 0.0885
2023-12-14 03:19 | 0.0885
2023-12-14 03:20 | 0.0888
2023-12-14 03:21 | 0.0885
2023-12-14 03:22 | 0.0886
2023-12-14 03:23 | 0.0888
2023-12-14 03:24 | 0.0887
2023-12-14 03:25 | 0.0885
2023-12-14 03:26 | 0.0885
2023-12-14 03:27 | 0.0884
2023-12-14 03:28 | 0.0885
2023-12-14 03:29 | 0.0884
2023-12-14 03:30 | 0.088
2023-12-14 03:31 | 0.0888
2023-12-14 03:32 | 0.088
2023-12-14 03:33 | 0.0883
2023-12-14 03:34 | 0.0885
2023-12-14 03:35 | 0.0886
2023-12-14 03:36 | 0.0884
2023-12-14 03:37 | 0.0887
2023-12-14 03:38 | 0.0888
2023-12-14 03:39 | 0.0887
2023-12-14 03:40 | 0.0887
2023-12-14 03:41 | 0.0882
2023-12-14 03:42 | 0.0886
2023-12-14 03:43 | 0.0885
2023-12-14 03:44 | 0.089
2023-12-14 03:45 | 0.0892
2023-12-14 03:46 | 0.0886
2023-12-14 03:47 | 0.0885
2023-12-14 03:48 | 0.0885
2023-12-14 03:49 | 0.0885
2023-12-14 03:50 | 0.0884
2023-12-14 03:51 | 0.0884
2023-12-14 03:52 | 0.0885
2023-12-14 03:53 | 0.0884
2023-12-14 03:54 | 0.0884
2023-12-14 03:55 | 0.0884
2023-12-14 03:56 | 0.0882
2023-12-14 03:57 | 0.0882
2023-12-14 03:58 | 0.0885
2023-12-14 03:59 | 0.0885
2023-12-14 04:00 | 0.0885
2023-12-14 04:01 | 0.0884
2023-12-14 04:02 | 0.0881
2023-12-14 04:03 | 0.0885
2023-12-14 04:04 | 0.0885
2023-12-14 04:05 | 0.0886
2023-12-14 04:06 | 0.0886
2023-12-14 04:07 | 0.0123
2023-12-14 04:08 | 0
2023-12-14 04:09 | 0
2023-12-14 04:10 | 0
2023-12-14 04:11 | 0
2023-12-14 04:12 | 0
2023-12-14 04:13 | 0.082
2023-12-14 04:14 | 0.0883
2023-12-14 04:15 | 0.0882
2023-12-14 04:16 | 0.0881
2023-12-14 04:17 | 0.0884
2023-12-14 04:18 | 0.0884
2023-12-14 04:19 | 0.0885
2023-12-14 04:20 | 0.0886
2023-12-14 04:21 | 0.0885
2023-12-14 04:22 | 0.0885
2023-12-14 04:23 | 0.0885
2023-12-14 04:24 | 0.0883
2023-12-14 04:25 | 0.0885
2023-12-14 04:26 | 0.0886
2023-12-14 04:27 | 0.0887
2023-12-14 04:28 | 0.0881
2023-12-14 04:29 | 0.0885
2023-12-14 04:30 | 0.0886
2023-12-14 04:31 | 0.0886
2023-12-14 04:32 | 0.0885
2023-12-14 04:33 | 0.0887
2023-12-14 04:34 | 0.0887
2023-12-14 04:35 | 0.0886
2023-12-14 04:36 | 0.0885
2023-12-14 04:37 | 0.0882
2023-12-14 04:38 | 0.0881
2023-12-14 04:39 | 0.0885
2023-12-14 04:40 | 0.0884
2023-12-14 04:41 | 0.0884
2023-12-14 04:42 | 0.0886
2023-12-14 04:43 | 0.0887
2023-12-14 04:44 | 0.0884
2023-12-14 04:45 | 0.0883
2023-12-14 04:46 | 0.0886
2023-12-14 04:47 | 0.0885
2023-12-14 04:48 | 0.0884
2023-12-14 04:49 | 0.0885
2023-12-14 04:50 | 0.0886
2023-12-14 04:51 | 0.0885
2023-12-14 04:52 | 0.0887
2023-12-14 04:53 | 0.0885
2023-12-14 04:54 | 0.0885
2023-12-14 04:55 | 0.0886
2023-12-14 04:56 | 0.0884
2023-12-14 04:57 | 0.0886
2023-12-14 04:58 | 0.0884
2023-12-14 04:59 | 0.0882
2023-12-14 05:00 | 0.0883
2023-12-14 05:01 | 0.0886
2023-12-14 05:02 | 0.0885
2023-12-14 05:03 | 0.0881
2023-12-14 05:04 | 0.0883
2023-12-14 05:05 | 0.0884
2023-12-14 05:06 | 0.0885
2023-12-14 05:07 | 0.0097
2023-12-14 05:08 | 0
2023-12-14 05:09 | 0
2023-12-14 05:10 | 0
2023-12-14 05:11 | 0
2023-12-14 05:12 | 0
2023-12-14 05:13 | 0.0851
2023-12-14 05:14 | 0.0881
2023-12-14 05:15 | 0.0883
2023-12-14 05:16 | 0.0883
2023-12-14 05:17 | 0.0882
2023-12-14 05:18 | 0.0884
2023-12-14 05:19 | 0.0881
2023-12-14 05:20 | 0.0882
2023-12-14 05:21 | 0.0884
2023-12-14 05:22 | 0.0883
2023-12-14 05:23 | 0.0885
2023-12-14 05:24 | 0.0885
2023-12-14 05:25 | 0.0887
2023-12-14 05:26 | 0.0888
2023-12-14 05:27 | 0.0885
2023-12-14 05:28 | 0.0885
2023-12-14 05:29 | 0.0884
2023-12-14 05:30 | 0.0886
2023-12-14 05:31 | 0.0882
2023-12-14 05:32 | 0.0882
2023-12-14 05:33 | 0.0883
2023-12-14 05:34 | 0.088
2023-12-14 05:35 | 0.088
2023-12-14 05:36 | 0.0883
2023-12-14 05:37 | 0.0884
2023-12-14 05:38 | 0.0884
2023-12-14 05:39 | 0.0883
2023-12-14 05:40 | 0.0882
2023-12-14 05:41 | 0.0881
2023-12-14 05:42 | 0.0879
2023-12-14 05:43 | 0.088
2023-12-14 05:44 | 0.0881
2023-12-14 05:45 | 0.0887
2023-12-14 05:46 | 0.0888
2023-12-14 05:47 | 0.0886
2023-12-14 05:48 | 0.0886
2023-12-14 05:49 | 0.0886
2023-12-14 05:50 | 0.0887
2023-12-14 05:51 | 0.089
2023-12-14 05:52 | 0.089
2023-12-14 05:53 | 0.0892
2023-12-14 05:54 | 0.089
2023-12-14 05:55 | 0.0889
2023-12-14 05:56 | 0.0888
2023-12-14 05:57 | 0.0888
2023-12-14 05:58 | 0.0887
2023-12-14 05:59 | 0.0888
2023-12-14 06:00 | 0.0886
2023-12-14 06:01 | 0.0883
2023-12-14 06:02 | 0.0884
2023-12-14 06:03 | 0.0882
2023-12-14 06:04 | 0.0883
2023-12-14 06:05 | 0.0883
2023-12-14 06:06 | 0.0883
2023-12-14 06:07 | 0.0024
2023-12-14 06:08 | 0
2023-12-14 06:09 | 0
2023-12-14 06:10 | 0
2023-12-14 06:11 | 0
2023-12-14 06:12 | 0
2023-12-14 06:13 | 0.0932
2023-12-14 06:14 | 0.088
2023-12-14 06:15 | 0.0883
2023-12-14 06:16 | 0.0881
2023-12-14 06:17 | 0.088
2023-12-14 06:18 | 0.088
2023-12-14 06:19 | 0.088
2023-12-14 06:20 | 0.0881
2023-12-14 06:21 | 0.0883
2023-12-14 06:22 | 0.0884
2023-12-14 06:23 | 0.0886
2023-12-14 06:24 | 0.0885
2023-12-14 06:25 | 0.0887
2023-12-14 06:26 | 0.0883
2023-12-14 06:27 | 0.0882
2023-12-14 06:28 | 0.0883
2023-12-14 06:29 | 0.0883
2023-12-14 06:30 | 0.0882
2023-12-14 06:31 | 0.0881
2023-12-14 06:32 | 0.0879
2023-12-14 06:33 | 0.0881
2023-12-14 06:34 | 0.0878
2023-12-14 06:35 | 0.087
2023-12-14 06:36 | 0.0872
2023-12-14 06:37 | 0.0873
2023-12-14 06:38 | 0.0873
2023-12-14 06:39 | 0.0876
2023-12-14 06:40 | 0.0873
2023-12-14 06:41 | 0.0873
2023-12-14 06:42 | 0.0877
2023-12-14 06:43 | 0.0876
2023-12-14 06:44 | 0.0876
2023-12-14 06:45 | 0.088
2023-12-14 06:46 | 0.0882
2023-12-14 06:47 | 0.0878
2023-12-14 06:48 | 0.0882
2023-12-14 06:49 | 0.088
2023-12-14 06:50 | 0.0883
2023-12-14 06:51 | 0.0885
2023-12-14 06:52 | 0.0884
2023-12-14 06:53 | 0.088
2023-12-14 06:54 | 0.0884
2023-12-14 06:55 | 0.088
2023-12-14 06:56 | 0.0881
2023-12-14 06:57 | 0.0882
2023-12-14 06:58 | 0.0884
2023-12-14 06:59 | 0.0882
2023-12-14 07:00 | 0.0878
2023-12-14 07:01 | 0.0878
2023-12-14 07:02 | 0.0872
2023-12-14 07:03 | 0.0874
2023-12-14 07:04 | 0.0875
2023-12-14 07:05 | 0.0875
2023-12-14 07:06 | 0.0853
2023-12-14 07:07 | 0
2023-12-14 07:08 | 0
2023-12-14 07:09 | 0
2023-12-14 07:10 | 0
2023-12-14 07:11 | 0
2023-12-14 07:12 | 0.0067
2023-12-14 07:13 | 0.0897
2023-12-14 07:14 | 0.0876
2023-12-14 07:15 | 0.0878
2023-12-14 07:16 | 0.0875
2023-12-14 07:17 | 0.0878
2023-12-14 07:18 | 0.0877
2023-12-14 07:19 | 0.0876
2023-12-14 07:20 | 0.0877
2023-12-14 07:21 | 0.0879
2023-12-14 07:22 | 0.0878
2023-12-14 07:23 | 0.0875
2023-12-14 07:24 | 0.0876
2023-12-14 07:25 | 0.0875
2023-12-14 07:26 | 0.0876
2023-12-14 07:27 | 0.0876
2023-12-14 07:28 | 0.0877
2023-12-14 07:29 | 0.087
2023-12-14 07:30 | 0.087
2023-12-14 07:31 | 0.087
2023-12-14 07:32 | 0.0872
2023-12-14 07:33 | 0.0872
2023-12-14 07:34 | 0.0872
2023-12-14 07:35 | 0.0877
2023-12-14 07:36 | 0.0878
2023-12-14 07:37 | 0.0884
2023-12-14 07:38 | 0.0883
2023-12-14 07:39 | 0.0885
2023-12-14 07:40 | 0.0883
2023-12-14 07:41 | 0.0881
2023-12-14 07:42 | 0.0883
2023-12-14 07:43 | 0.0882
2023-12-14 07:44 | 0.0884
2023-12-14 07:45 | 0.088
2023-12-14 07:46 | 0.0882
2023-12-14 07:47 | 0.0881
2023-12-14 07:48 | 0.088
2023-12-14 07:49 | 0.0881
2023-12-14 07:50 | 0.088
2023-12-14 07:51 | 0.0877
2023-12-14 07:52 | 0.088
2023-12-14 07:53 | 0.0879
2023-12-14 07:54 | 0.0881
2023-12-14 07:55 | 0.0882
2023-12-14 07:56 | 0.088
2023-12-14 07:57 | 0.088
2023-12-14 07:58 | 0.088
2023-12-14 07:59 | 0.0881
2023-12-14 08:00 | 0.088
2023-12-14 08:01 | 0.0878
2023-12-14 08:02 | 0.0883
2023-12-14 08:03 | 0.0881
2023-12-14 08:04 | 0.0881
2023-12-14 08:05 | 0.088
2023-12-14 08:06 | 0.0878
2023-12-14 08:07 | 0.0056
2023-12-14 08:08 | 0
2023-12-14 08:09 | 0
2023-12-14 08:10 | 0
2023-12-14 08:11 | 0
2023-12-14 08:12 | 0
2023-12-14 08:13 | 0.0871
2023-12-14 08:14 | 0.0877
2023-12-14 08:15 | 0.0878
2023-12-14 08:16 | 0.0879
2023-12-14 08:17 | 0.088
2023-12-14 08:18 | 0.088
2023-12-14 08:19 | 0.0879
2023-12-14 08:20 | 0.0875
2023-12-14 08:21 | 0.0876
2023-12-14 08:22 | 0.0881
2023-12-14 08:23 | 0.0879
2023-12-14 08:24 | 0.0881
2023-12-14 08:25 | 0.0882
2023-12-14 08:26 | 0.0882
2023-12-14 08:27 | 0.0881
2023-12-14 08:28 | 0.0883
2023-12-14 08:29 | 0.0882
2023-12-14 08:30 | 0.0879
2023-12-14 08:31 | 0.0881
2023-12-14 08:32 | 0.0876
2023-12-14 08:33 | 0.0876
2023-12-14 08:34 | 0.0877
2023-12-14 08:35 | 0.0884
2023-12-14 08:36 | 0.0885
2023-12-14 08:37 | 0.088
2023-12-14 08:38 | 0.0879
2023-12-14 08:39 | 0.0883
2023-12-14 08:40 | 0.0881
2023-12-14 08:41 | 0.0882
2023-12-14 08:42 | 0.088
2023-12-14 08:43 | 0.0883
2023-12-14 08:44 | 0.0882
2023-12-14 08:45 | 0.0884
2023-12-14 08:46 | 0.0882
2023-12-14 08:47 | 0.0883
2023-12-14 08:48 | 0.0888
2023-12-14 08:49 | 0.0885
2023-12-14 08:50 | 0.0881
2023-12-14 08:51 | 0.0881
2023-12-14 08:52 | 0.0881
2023-12-14 08:53 | 0.0884
2023-12-14 08:54 | 0.0882
2023-12-14 08:55 | 0.0885
2023-12-14 08:56 | 0.0886
2023-12-14 08:57 | 0.0884
2023-12-14 08:58 | 0.0882
2023-12-14 08:59 | 0.0875
2023-12-14 09:00 | 0.088
2023-12-14 09:01 | 0.0884
2023-12-14 09:02 | 0.0881
2023-12-14 09:03 | 0.0883
2023-12-14 09:04 | 0.0883
2023-12-14 09:05 | 0.088
2023-12-14 09:06 | 0.0882
2023-12-14 09:07 | 0.0259
2023-12-14 09:08 | 0
2023-12-14 09:09 | 0
2023-12-14 09:10 | 0
2023-12-14 09:11 | 0
2023-12-14 09:12 | 0
2023-12-14 09:13 | 0.0655
2023-12-14 09:14 | 0.0874
2023-12-14 09:15 | 0.0878
2023-12-14 09:16 | 0.0882
2023-12-14 09:17 | 0.0884
2023-12-14 09:18 | 0.0879
2023-12-14 09:19 | 0.0883
2023-12-14 09:20 | 0.0881
2023-12-14 09:21 | 0.0882
2023-12-14 09:22 | 0.0882
2023-12-14 09:23 | 0.0881
2023-12-14 09:24 | 0.0882
2023-12-14 09:25 | 0.0883
2023-12-14 09:26 | 0.0885
2023-12-14 09:27 | 0.0886
2023-12-14 09:28 | 0.0885
2023-12-14 09:29 | 0.0883
2023-12-14 09:30 | 0.0886
2023-12-14 09:31 | 0.0886
2023-12-14 09:32 | 0.0883
2023-12-14 09:33 | 0.0884
2023-12-14 09:34 | 0.0884
2023-12-14 09:35 | 0.0884
2023-12-14 09:36 | 0.0882
2023-12-14 09:37 | 0.0882
2023-12-14 09:38 | 0.0883
2023-12-14 09:39 | 0.0881
2023-12-14 09:40 | 0.0881
2023-12-14 09:41 | 0.0878
2023-12-14 09:42 | 0.0883
2023-12-14 09:43 | 0.0885
2023-12-14 09:44 | 0.0876
2023-12-14 09:45 | 0.0873
2023-12-14 09:46 | 0.0875
2023-12-14 09:47 | 0.0875
2023-12-14 09:48 | 0.0883
2023-12-14 09:49 | 0.0888
2023-12-14 09:50 | 0.0886
2023-12-14 09:51 | 0.0886
2023-12-14 09:52 | 0.0887
2023-12-14 09:53 | 0.0888
2023-12-14 09:54 | 0.0886
2023-12-14 09:55 | 0.0887
2023-12-14 09:56 | 0.0883
2023-12-14 09:57 | 0.0879
2023-12-14 09:58 | 0.0877
2023-12-14 09:59 | 0.0882
2023-12-14 10:00 | 0.0881
2023-12-14 10:01 | 0.0882
2023-12-14 10:02 | 0.0882
2023-12-14 10:03 | 0.0879
2023-12-14 10:04 | 0.0886
2023-12-14 10:05 | 0.0885
2023-12-14 10:06 | 0.0884
2023-12-14 10:07 | 0.0581
2023-12-14 10:08 | 0
2023-12-14 10:09 | 0
2023-12-14 10:10 | 0
2023-12-14 10:11 | 0
2023-12-14 10:12 | 0
2023-12-14 10:13 | 0.0327
2023-12-14 10:14 | 0.0879
2023-12-14 10:15 | 0.0879
2023-12-14 10:16 | 0.0884
2023-12-14 10:17 | 0.0879
2023-12-14 10:18 | 0.0877
2023-12-14 10:19 | 0.0882
2023-12-14 10:20 | 0.0882
2023-12-14 10:21 | 0.0881
2023-12-14 10:22 | 0.0883
2023-12-14 10:23 | 0.0884
2023-12-14 10:24 | 0.0884
2023-12-14 10:25 | 0.0881
2023-12-14 10:26 | 0.0878
2023-12-14 10:27 | 0.024
2023-12-14 10:28 | 0
2023-12-14 10:29 | 0
2023-12-14 10:30 | 0
2023-12-14 10:31 | 0
2023-12-14 10:32 | 0
2023-12-14 10:33 | 0
2023-12-14 10:34 | 0
2023-12-14 10:35 | 0
2023-12-14 10:36 | 0
2023-12-14 10:37 | 0
2023-12-14 10:38 | 0
2023-12-14 10:39 | 0
2023-12-14 10:40 | 0
2023-12-14 10:41 | 0
2023-12-14 10:42 | 0
2023-12-14 10:43 | 0
2023-12-14 10:44 | 0
2023-12-14 10:45 | 0
2023-12-14 10:46 | 0
2023-12-14 10:47 | 0
2023-12-14 10:48 | 0
2023-12-14 10:49 | 0
2023-12-14 10:50 | 0
2023-12-14 10:51 | 0
2023-12-14 10:52 | 0
2023-12-14 10:53 | 0
2023-12-14 10:54 | 0
2023-12-14 10:55 | 0
2023-12-14 10:56 | 0
2023-12-14 10:57 | 0
2023-12-14 10:58 | 0
2023-12-14 10:59 | 0
2023-12-14 11:00 | 0
2023-12-14 11:01 | 0
2023-12-14 11:02 | 0
2023-12-14 11:03 | 0
2023-12-14 11:04 | 0
2023-12-14 11:05 | 0
2023-12-14 11:06 | 0
2023-12-14 11:07 | 0
2023-12-14 11:08 | 0
2023-12-14 11:09 | 0
2023-12-14 11:10 | 0
2023-12-14 11:11 | 0
2023-12-14 11:12 | 0
2023-12-14 11:13 | 0
2023-12-14 11:14 | 0
2023-12-14 11:15 | 0.0458
2023-12-14 11:16 | 0.0875
2023-12-14 11:17 | 0.0881
2023-12-14 11:18 | 0.0885
2023-12-14 11:19 | 0.0883
2023-12-14 11:20 | 0.0883
2023-12-14 11:21 | 0.0883
2023-12-14 11:22 | 0.0888
2023-12-14 11:23 | 0.089
2023-12-14 11:24 | 0.0886
2023-12-14 11:25 | 0.0881
2023-12-14 11:26 | 0.0886
2023-12-14 11:27 | 0.0567
2023-12-14 11:28 | 0
2023-12-14 11:29 | 0
2023-12-14 11:30 | 0
2023-12-14 11:31 | 0
2023-12-14 11:32 | 0
2023-12-14 11:33 | 0
2023-12-14 11:34 | 0
2023-12-14 11:35 | 0
2023-12-14 11:36 | 0
2023-12-14 11:37 | 0
2023-12-14 11:38 | 0
2023-12-14 11:39 | 0
2023-12-14 11:40 | 0
2023-12-14 11:41 | 0
2023-12-14 11:42 | 0
2023-12-14 11:43 | 0
2023-12-14 11:44 | 0
2023-12-14 11:45 | 0
2023-12-14 11:46 | 0
2023-12-14 11:47 | 0
2023-12-14 11:48 | 0
2023-12-14 11:49 | 0
2023-12-14 11:50 | 0
2023-12-14 11:51 | 0
2023-12-14 11:52 | 0
2023-12-14 11:53 | 0
2023-12-14 11:54 | 0
2023-12-14 11:55 | 0
2023-12-14 11:56 | 0
2023-12-14 11:57 | 0
2023-12-14 11:58 | 0
2023-12-14 11:59 | 0
2023-12-14 12:00 | 0
2023-12-14 12:01 | 0
2023-12-14 12:02 | 0
2023-12-14 12:03 | 0
2023-12-14 12:04 | 0
2023-12-14 12:05 | 0
2023-12-14 12:06 | 0
2023-12-14 12:07 | 0
2023-12-14 12:08 | 0
2023-12-14 12:09 | 0
2023-12-14 12:10 | 0
2023-12-14 12:11 | 0
2023-12-14 12:12 | 0
2023-12-14 12:13 | 0
2023-12-14 12:14 | 0
2023-12-14 12:15 | 0.0147
2023-12-14 12:16 | 0.0869
2023-12-14 12:17 | 0.0876
2023-12-14 12:18 | 0.0881
2023-12-14 12:19 | 0.0878
2023-12-14 12:20 | 0.0881
2023-12-14 12:21 | 0.0878
2023-12-14 12:22 | 0.0884
2023-12-14 12:23 | 0.0883
2023-12-14 12:24 | 0.0881
2023-12-14 12:25 | 0.0886
2023-12-14 12:26 | 0.0881
2023-12-14 12:27 | 0.0869
2023-12-14 12:28 | 0
2023-12-14 12:29 | 0
2023-12-14 12:30 | 0
2023-12-14 12:31 | 0
2023-12-14 12:32 | 0
2023-12-14 12:33 | 0
2023-12-14 12:34 | 0
2023-12-14 12:35 | 0
2023-12-14 12:36 | 0
2023-12-14 12:37 | 0
2023-12-14 12:38 | 0
2023-12-14 12:39 | 0
2023-12-14 12:40 | 0
2023-12-14 12:41 | 0
2023-12-14 12:42 | 0
2023-12-14 12:43 | 0
2023-12-14 12:44 | 0
2023-12-14 12:45 | 0
2023-12-14 12:46 | 0
2023-12-14 12:47 | 0
2023-12-14 12:48 | 0
2023-12-14 12:49 | 0
2023-12-14 12:50 | 0
2023-12-14 12:51 | 0
2023-12-14 12:52 | 0
2023-12-14 12:53 | 0
2023-12-14 12:54 | 0
2023-12-14 12:55 | 0
2023-12-14 12:56 | 0
2023-12-14 12:57 | 0
2023-12-14 12:58 | 0
2023-12-14 12:59 | 0
2023-12-14 13:00 | 0
2023-12-14 13:01 | 0
2023-12-14 13:02 | 0
2023-12-14 13:03 | 0
2023-12-14 13:04 | 0
2023-12-14 13:05 | 0
2023-12-14 13:06 | 0
2023-12-14 13:07 | 0
2023-12-14 13:08 | 0
2023-12-14 13:09 | 0
2023-12-14 13:10 | 0
2023-12-14 13:11 | 0
2023-12-14 13:12 | 0
2023-12-14 13:13 | 0
2023-12-14 13:14 | 0
2023-12-14 13:15 | 0
2023-12-14 13:16 | 0.0715
2023-12-14 13:17 | 0.0867
2023-12-14 13:18 | 0.0872
2023-12-14 13:19 | 0.0875
2023-12-14 13:20 | 0.087
2023-12-14 13:21 | 0.0875
2023-12-14 13:22 | 0.0869
2023-12-14 13:23 | 0.0875
2023-12-14 13:24 | 0.0876
2023-12-14 13:25 | 0.0874
2023-12-14 13:26 | 0.0881
2023-12-14 13:27 | 0.088
2023-12-14 13:28 | 0.0276
2023-12-14 13:29 | 0
2023-12-14 13:30 | 0
2023-12-14 13:31 | 0
2023-12-14 13:32 | 0
2023-12-14 13:33 | 0
2023-12-14 13:34 | 0
2023-12-14 13:35 | 0
2023-12-14 13:36 | 0
2023-12-14 13:37 | 0
2023-12-14 13:38 | 0
2023-12-14 13:39 | 0
2023-12-14 13:40 | 0
2023-12-14 13:41 | 0
2023-12-14 13:42 | 0
2023-12-14 13:43 | 0
2023-12-14 13:44 | 0
2023-12-14 13:45 | 0
2023-12-14 13:46 | 0
2023-12-14 13:47 | 0
2023-12-14 13:48 | 0
2023-12-14 13:49 | 0
2023-12-14 13:50 | 0
2023-12-14 13:51 | 0
2023-12-14 13:52 | 0
2023-12-14 13:53 | 0
2023-12-14 13:54 | 0
2023-12-14 13:55 | 0
2023-12-14 13:56 | 0
2023-12-14 13:57 | 0
2023-12-14 13:58 | 0
2023-12-14 13:59 | 0
2023-12-14 14:00 | 0
2023-12-14 14:01 | 0
2023-12-14 14:02 | 0
2023-12-14 14:03 | 0
2023-12-14 14:04 | 0
2023-12-14 14:05 | 0
2023-12-14 14:06 | 0
2023-12-14 14:07 | 0
2023-12-14 14:08 | 0
2023-12-14 14:09 | 0
2023-12-14 14:10 | 0
2023-12-14 14:11 | 0
2023-12-14 14:12 | 0
2023-12-14 14:13 | 0
2023-12-14 14:14 | 0
2023-12-14 14:15 | 0
2023-12-14 14:16 | 0.0453
2023-12-14 14:17 | 0.0864
2023-12-14 14:18 | 0.0868
2023-12-14 14:19 | 0.0872
2023-12-14 14:20 | 0.0876
2023-12-14 14:21 | 0.0873
2023-12-14 14:22 | 0.087
2023-12-14 14:23 | 0.0873
2023-12-14 14:24 | 0.0876
2023-12-14 14:25 | 0.0881
2023-12-14 14:26 | 0.0878
2023-12-14 14:27 | 0.0878
2023-12-14 14:28 | 0.053
2023-12-14 14:29 | 0
2023-12-14 14:30 | 0
2023-12-14 14:31 | 0
2023-12-14 14:32 | 0
2023-12-14 14:33 | 0
2023-12-14 14:34 | 0
2023-12-14 14:35 | 0
2023-12-14 14:36 | 0
2023-12-14 14:37 | 0
2023-12-14 14:38 | 0
2023-12-14 14:39 | 0
2023-12-14 14:40 | 0
2023-12-14 14:41 | 0
2023-12-14 14:42 | 0
2023-12-14 14:43 | 0
2023-12-14 14:44 | 0
2023-12-14 14:45 | 0
2023-12-14 14:46 | 0
2023-12-14 14:47 | 0
2023-12-14 14:48 | 0
2023-12-14 14:49 | 0
2023-12-14 14:50 | 0
2023-12-14 14:51 | 0
2023-12-14 14:52 | 0
2023-12-14 14:53 | 0
2023-12-14 14:54 | 0
2023-12-14 14:55 | 0
2023-12-14 14:56 | 0
2023-12-14 14:57 | 0
2023-12-14 14:58 | 0
2023-12-14 14:59 | 0
2023-12-14 15:00 | 0
2023-12-14 15:01 | 0
2023-12-14 15:02 | 0
2023-12-14 15:03 | 0
2023-12-14 15:04 | 0
2023-12-14 15:05 | 0
2023-12-14 15:06 | 0
2023-12-14 15:07 | 0
2023-12-14 15:08 | 0
2023-12-14 15:09 | 0
2023-12-14 15:10 | 0
2023-12-14 15:11 | 0
2023-12-14 15:12 | 0
2023-12-14 15:13 | 0
2023-12-14 15:14 | 0
2023-12-14 15:15 | 0
2023-12-14 15:16 | 0.0227
2023-12-14 15:17 | 0.0864
2023-12-14 15:18 | 0.0867
2023-12-14 15:19 | 0.0867
2023-12-14 15:20 | 0.087
2023-12-14 15:21 | 0.0872
2023-12-14 15:22 | 0.0872
2023-12-14 15:23 | 0.0871
2023-12-14 15:24 | 0.0868
2023-12-14 15:25 | 0.0869
2023-12-14 15:26 | 0.0871
2023-12-14 15:27 | 0.087
2023-12-14 15:28 | 0.0761
2023-12-14 15:29 | 0
2023-12-14 15:30 | 0
2023-12-14 15:31 | 0
2023-12-14 15:32 | 0
2023-12-14 15:33 | 0
2023-12-14 15:34 | 0
2023-12-14 15:35 | 0
2023-12-14 15:36 | 0
2023-12-14 15:37 | 0
2023-12-14 15:38 | 0
2023-12-14 15:39 | 0
2023-12-14 15:40 | 0
2023-12-14 15:41 | 0
2023-12-14 15:42 | 0
2023-12-14 15:43 | 0
2023-12-14 15:44 | 0
2023-12-14 15:45 | 0
2023-12-14 15:46 | 0
2023-12-14 15:47 | 0
2023-12-14 15:48 | 0
2023-12-14 15:49 | 0
2023-12-14 15:50 | 0
2023-12-14 15:51 | 0
2023-12-14 15:52 | 0
2023-12-14 15:53 | 0
2023-12-14 15:54 | 0
2023-12-14 15:55 | 0
2023-12-14 15:56 | 0
2023-12-14 15:57 | 0
2023-12-14 15:58 | 0
2023-12-14 15:59 | 0
2023-12-14 16:00 | 0
2023-12-14 16:01 | 0
2023-12-14 16:02 | 0
2023-12-14 16:03 | 0
2023-12-14 16:04 | 0
2023-12-14 16:05 | 0
2023-12-14 16:06 | 0
2023-12-14 16:07 | 0
2023-12-14 16:08 | 0
2023-12-14 16:09 | 0
2023-12-14 16:10 | 0
2023-12-14 16:11 | 0
2023-12-14 16:12 | 0
2023-12-14 16:13 | 0
2023-12-14 16:14 | 0
2023-12-14 16:15 | 0
2023-12-14 16:16 | 0
2023-12-14 16:17 | 0.0841
2023-12-14 16:18 | 0.0857
2023-12-14 16:19 | 0.0859
2023-12-14 16:20 | 0.0861
2023-12-14 16:21 | 0.0863
2023-12-14 16:22 | 0.0865
2023-12-14 16:23 | 0.0862
2023-12-14 16:24 | 0.0867
2023-12-14 16:25 | 0.0867
2023-12-14 16:26 | 0.0868
2023-12-14 16:27 | 0.0868
2023-12-14 16:28 | 0.0869
2023-12-14 16:29 | 0.0122
2023-12-14 16:30 | 0
2023-12-14 16:31 | 0
2023-12-14 16:32 | 0
2023-12-14 16:33 | 0
2023-12-14 16:34 | 0
2023-12-14 16:35 | 0
2023-12-14 16:36 | 0
2023-12-14 16:37 | 0
2023-12-14 16:38 | 0
2023-12-14 16:39 | 0
2023-12-14 16:40 | 0
2023-12-14 16:41 | 0
2023-12-14 16:42 | 0
2023-12-14 16:43 | 0
2023-12-14 16:44 | 0
2023-12-14 16:45 | 0
2023-12-14 16:46 | 0
2023-12-14 16:47 | 0
2023-12-14 16:48 | 0
2023-12-14 16:49 | 0
2023-12-14 16:50 | 0
2023-12-14 16:51 | 0
2023-12-14 16:52 | 0
2023-12-14 16:53 | 0
2023-12-14 16:54 | 0
2023-12-14 16:55 | 0
2023-12-14 16:56 | 0
2023-12-14 16:57 | 0
2023-12-14 16:58 | 0
2023-12-14 16:59 | 0
2023-12-14 17:00 | 0
2023-12-14 17:01 | 0
2023-12-14 17:02 | 0
2023-12-14 17:03 | 0
2023-12-14 17:04 | 0
2023-12-14 17:05 | 0
2023-12-14 17:06 | 0
2023-12-14 17:07 | 0
2023-12-14 17:08 | 0
2023-12-14 17:09 | 0
2023-12-14 17:10 | 0
2023-12-14 17:11 | 0
2023-12-14 17:12 | 0
2023-12-14 17:13 | 0
2023-12-14 17:14 | 0
2023-12-14 17:15 | 0
2023-12-14 17:16 | 0
2023-12-14 17:17 | 0.0635
2023-12-14 17:18 | 0.0848
2023-12-14 17:19 | 0.0853
2023-12-14 17:20 | 0.0854
2023-12-14 17:21 | 0.0855
2023-12-14 17:22 | 0.0854
2023-12-14 17:23 | 0.0856
2023-12-14 17:24 | 0.0856
2023-12-14 17:25 | 0.0854
2023-12-14 17:26 | 0.0854
2023-12-14 17:27 | 0.0853
2023-12-14 17:28 | 0.0854
2023-12-14 17:29 | 0.0335
2023-12-14 17:30 | 0
2023-12-14 17:31 | 0
2023-12-14 17:32 | 0
2023-12-14 17:33 | 0
2023-12-14 17:34 | 0
2023-12-14 17:35 | 0
2023-12-14 17:36 | 0
2023-12-14 17:37 | 0
2023-12-14 17:38 | 0
2023-12-14 17:39 | 0
2023-12-14 17:40 | 0
2023-12-14 17:41 | 0
2023-12-14 17:42 | 0
2023-12-14 17:43 | 0
2023-12-14 17:44 | 0
2023-12-14 17:45 | 0
2023-12-14 17:46 | 0
2023-12-14 17:47 | 0
2023-12-14 17:48 | 0
2023-12-14 17:49 | 0
2023-12-14 17:50 | 0
2023-12-14 17:51 | 0
2023-12-14 17:52 | 0
2023-12-14 17:53 | 0
2023-12-14 17:54 | 0
2023-12-14 17:55 | 0
2023-12-14 17:56 | 0
2023-12-14 17:57 | 0
2023-12-14 17:58 | 0
2023-12-14 17:59 | 0
2023-12-14 18:00 | 0
2023-12-14 18:01 | 0
2023-12-14 18:02 | 0
2023-12-14 18:03 | 0
2023-12-14 18:04 | 0
2023-12-14 18:05 | 0
2023-12-14 18:06 | 0
2023-12-14 18:07 | 0
2023-12-14 18:08 | 0
2023-12-14 18:09 | 0
2023-12-14 18:10 | 0
2023-12-14 18:11 | 0
2023-12-14 18:12 | 0
2023-12-14 18:13 | 0
2023-12-14 18:14 | 0
2023-12-14 18:15 | 0
2023-12-14 18:16 | 0
2023-12-14 18:17 | 0.0446
2023-12-14 18:18 | 0.086
2023-12-14 18:19 | 0.0867
2023-12-14 18:20 | 0.0869
2023-12-14 18:21 | 0.0868
2023-12-14 18:22 | 0.087
2023-12-14 18:23 | 0.087
2023-12-14 18:24 | 0.0872
2023-12-14 18:25 | 0.0872
2023-12-14 18:26 | 0.0874
2023-12-14 18:27 | 0.0873
2023-12-14 18:28 | 0.0872
2023-12-14 18:29 | 0.0523
2023-12-14 18:30 | 0
2023-12-14 18:31 | 0
2023-12-14 18:32 | 0
2023-12-14 18:33 | 0
2023-12-14 18:34 | 0
2023-12-14 18:35 | 0
2023-12-14 18:36 | 0
2023-12-14 18:37 | 0
2023-12-14 18:38 | 0
2023-12-14 18:39 | 0
2023-12-14 18:40 | 0
2023-12-14 18:41 | 0
2023-12-14 18:42 | 0
2023-12-14 18:43 | 0
2023-12-14 18:44 | 0
2023-12-14 18:45 | 0
2023-12-14 18:46 | 0
2023-12-14 18:47 | 0
2023-12-14 18:48 | 0
2023-12-14 18:49 | 0
2023-12-14 18:50 | 0
2023-12-14 18:51 | 0
2023-12-14 18:52 | 0
2023-12-14 18:53 | 0
2023-12-14 18:54 | 0
2023-12-14 18:55 | 0
2023-12-14 18:56 | 0
2023-12-14 18:57 | 0
2023-12-14 18:58 | 0
2023-12-14 18:59 | 0
2023-12-14 19:00 | 0
2023-12-14 19:01 | 0
2023-12-14 19:02 | 0
2023-12-14 19:03 | 0
2023-12-14 19:04 | 0
2023-12-14 19:05 | 0
2023-12-14 19:06 | 0
2023-12-14 19:07 | 0
2023-12-14 19:08 | 0
2023-12-14 19:09 | 0
2023-12-14 19:10 | 0
2023-12-14 19:11 | 0
2023-12-14 19:12 | 0
2023-12-14 19:13 | 0
2023-12-14 19:14 | 0
2023-12-14 19:15 | 0
2023-12-14 19:16 | 0
2023-12-14 19:17 | 0.0272
2023-12-14 19:18 | 0.0861
2023-12-14 19:19 | 0.0865
2023-12-14 19:20 | 0.087
2023-12-14 19:21 | 0.0871
2023-12-14 19:22 | 0.0872
2023-12-14 19:23 | 0.0868
2023-12-14 19:24 | 0.0869
2023-12-14 19:25 | 0.0867
2023-12-14 19:26 | 0.0867
2023-12-14 19:27 | 0.0869
2023-12-14 19:28 | 0.0872
2023-12-14 19:29 | 0.0701
2023-12-14 19:30 | 0
2023-12-14 19:31 | 0
2023-12-14 19:32 | 0
2023-12-14 19:33 | 0
2023-12-14 19:34 | 0
2023-12-14 19:35 | 0
2023-12-14 19:36 | 0
2023-12-14 19:37 | 0
2023-12-14 19:38 | 0
2023-12-14 19:39 | 0
2023-12-14 19:40 | 0
2023-12-14 19:41 | 0
2023-12-14 19:42 | 0
2023-12-14 19:43 | 0
2023-12-14 19:44 | 0
2023-12-14 19:45 | 0
2023-12-14 19:46 | 0
2023-12-14 19:47 | 0
2023-12-14 19:48 | 0
2023-12-14 19:49 | 0
2023-12-14 19:50 | 0
2023-12-14 19:51 | 0
2023-12-14 19:52 | 0
2023-12-14 19:53 | 0
2023-12-14 19:54 | 0
2023-12-14 19:55 | 0
2023-12-14 19:56 | 0
2023-12-14 19:57 | 0
2023-12-14 19:58 | 0
2023-12-14 19:59 | 0
2023-12-14 20:00 | 0
2023-12-14 20:01 | 0
2023-12-14 20:02 | 0
2023-12-14 20:03 | 0
2023-12-14 20:04 | 0
2023-12-14 20:05 | 0
2023-12-14 20:06 | 0
2023-12-14 20:07 | 0
2023-12-14 20:08 | 0
2023-12-14 20:09 | 0
2023-12-14 20:10 | 0
2023-12-14 20:11 | 0
2023-12-14 20:12 | 0
2023-12-14 20:13 | 0
2023-12-14 20:14 | 0
2023-12-14 20:15 | 0
2023-12-14 20:16 | 0
2023-12-14 20:17 | 0.0095
2023-12-14 20:18 | 0.0856
2023-12-14 20:19 | 0.0861
2023-12-14 20:20 | 0.0865
2023-12-14 20:21 | 0.0864
2023-12-14 20:22 | 0.0868
2023-12-14 20:23 | 0.0869
2023-12-14 20:24 | 0.0871
2023-12-14 20:25 | 0.0872
2023-12-14 20:26 | 0.0873
2023-12-14 20:27 | 0.0871
2023-12-14 20:28 | 0.0872
2023-12-14 20:29 | 0.0872
2023-12-14 20:30 | 0.0004
2023-12-14 20:31 | 0
2023-12-14 20:32 | 0
2023-12-14 20:33 | 0
2023-12-14 20:34 | 0
2023-12-14 20:35 | 0
2023-12-14 20:36 | 0
2023-12-14 20:37 | 0
2023-12-14 20:38 | 0
2023-12-14 20:39 | 0
2023-12-14 20:40 | 0
2023-12-14 20:41 | 0
2023-12-14 20:42 | 0
2023-12-14 20:43 | 0
2023-12-14 20:44 | 0
2023-12-14 20:45 | 0
2023-12-14 20:46 | 0
2023-12-14 20:47 | 0
2023-12-14 20:48 | 0
2023-12-14 20:49 | 0
2023-12-14 20:50 | 0
2023-12-14 20:51 | 0
2023-12-14 20:52 | 0
2023-12-14 20:53 | 0
2023-12-14 20:54 | 0
2023-12-14 20:55 | 0
2023-12-14 20:56 | 0
2023-12-14 20:57 | 0
2023-12-14 20:58 | 0
2023-12-14 20:59 | 0
2023-12-14 21:00 | 0
2023-12-14 21:01 | 0
2023-12-14 21:02 | 0
2023-12-14 21:03 | 0
2023-12-14 21:04 | 0
2023-12-14 21:05 | 0
2023-12-14 21:06 | 0
2023-12-14 21:07 | 0
2023-12-14 21:08 | 0
2023-12-14 21:09 | 0
2023-12-14 21:10 | 0
2023-12-14 21:11 | 0
2023-12-14 21:12 | 0
2023-12-14 21:13 | 0
2023-12-14 21:14 | 0
2023-12-14 21:15 | 0
2023-12-14 21:16 | 0
2023-12-14 21:17 | 0
2023-12-14 21:18 | 0.082
2023-12-14 21:19 | 0.0856
2023-12-14 21:20 | 0.0862
2023-12-14 21:21 | 0.0861
2023-12-14 21:22 | 0.0865
2023-12-14 21:23 | 0.0866
2023-12-14 21:24 | 0.0867
2023-12-14 21:25 | 0.0869
2023-12-14 21:26 | 0.0871
2023-12-14 21:27 | 0.0873
2023-12-14 21:28 | 0.0875
2023-12-14 21:29 | 0.0872
2023-12-14 21:30 | 0.0127
2023-12-14 21:31 | 0
2023-12-14 21:32 | 0
2023-12-14 21:33 | 0
2023-12-14 21:34 | 0
2023-12-14 21:35 | 0
2023-12-14 21:36 | 0
2023-12-14 21:37 | 0
2023-12-14 21:38 | 0
2023-12-14 21:39 | 0
2023-12-14 21:40 | 0
2023-12-14 21:41 | 0
2023-12-14 21:42 | 0
2023-12-14 21:43 | 0
2023-12-14 21:44 | 0
2023-12-14 21:45 | 0
2023-12-14 21:46 | 0
2023-12-14 21:47 | 0
2023-12-14 21:48 | 0
2023-12-14 21:49 | 0
2023-12-14 21:50 | 0
2023-12-14 21:51 | 0
2023-12-14 21:52 | 0
2023-12-14 21:53 | 0
2023-12-14 21:54 | 0
2023-12-14 21:55 | 0
2023-12-14 21:56 | 0
2023-12-14 21:57 | 0
2023-12-14 21:58 | 0
2023-12-14 21:59 | 0
2023-12-14 22:00 | 0
2023-12-14 22:01 | 0
2023-12-14 22:02 | 0
2023-12-14 22:03 | 0
2023-12-14 22:04 | 0
2023-12-14 22:05 | 0
2023-12-14 22:06 | 0
2023-12-14 22:07 | 0
2023-12-14 22:08 | 0
2023-12-14 22:09 | 0
2023-12-14 22:10 | 0
2023-12-14 22:11 | 0
2023-12-14 22:12 | 0
2023-12-14 22:13 | 0
2023-12-14 22:14 | 0
2023-12-14 22:15 | 0
2023-12-14 22:16 | 0
2023-12-14 22:17 | 0
2023-12-14 22:18 | 0.0749
2023-12-14 22:19 | 0.0862
2023-12-14 22:20 | 0.0867
2023-12-14 22:21 | 0.0872
2023-12-14 22:22 | 0.0874
2023-12-14 22:23 | 0.0874
2023-12-14 22:24 | 0.0877
2023-12-14 22:25 | 0.0874
2023-12-14 22:26 | 0.0877
2023-12-14 22:27 | 0.0875
2023-12-14 22:28 | 0.0874
2023-12-14 22:29 | 0.0878
2023-12-14 22:30 | 0.0188
2023-12-14 22:31 | 0
2023-12-14 22:32 | 0
2023-12-14 22:33 | 0
2023-12-14 22:34 | 0
2023-12-14 22:35 | 0
2023-12-14 22:36 | 0
2023-12-14 22:37 | 0
2023-12-14 22:38 | 0
2023-12-14 22:39 | 0
2023-12-14 22:40 | 0
2023-12-14 22:41 | 0
2023-12-14 22:42 | 0
2023-12-14 22:43 | 0
2023-12-14 22:44 | 0
2023-12-14 22:45 | 0
2023-12-14 22:46 | 0
2023-12-14 22:47 | 0
2023-12-14 22:48 | 0
2023-12-14 22:49 | 0
2023-12-14 22:50 | 0
2023-12-14 22:51 | 0
2023-12-14 22:52 | 0
2023-12-14 22:53 | 0
2023-12-14 22:54 | 0
2023-12-14 22:55 | 0
2023-12-14 22:56 | 0
2023-12-14 22:57 | 0
2023-12-14 22:58 | 0
2023-12-14 22:59 | 0
2023-12-14 23:00 | 0
2023-12-14 23:01 | 0
2023-12-14 23:02 | 0
2023-12-14 23:03 | 0
2023-12-14 23:04 | 0
2023-12-14 23:05 | 0
2023-12-14 23:06 | 0
2023-12-14 23:07 | 0
2023-12-14 23:08 | 0
2023-12-14 23:09 | 0
2023-12-14 23:10 | 0
2023-12-14 23:11 | 0
2023-12-14 23:12 | 0
2023-12-14 23:13 | 0
2023-12-14 23:14 | 0
2023-12-14 23:15 | 0
2023-12-14 23:16 | 0
2023-12-14 23:17 | 0
2023-12-14 23:18 | 0.075
2023-12-14 23:19 | 0.0868
2023-12-14 23:20 | 0.0871
2023-12-14 23:21 | 0.0873
2023-12-14 23:22 | 0.0872
2023-12-14 23:23 | 0.0871
2023-12-14 23:24 | 0.0871
2023-12-14 23:25 | 0.0873
2023-12-14 23:26 | 0.0876
2023-12-14 23:27 | 0.0871
2023-12-14 23:28 | 0.0875
2023-12-14 23:29 | 0.0877
2023-12-14 23:30 | 0.0198
2023-12-14 23:31 | 0
2023-12-14 23:32 | 0
2023-12-14 23:33 | 0
2023-12-14 23:34 | 0
2023-12-14 23:35 | 0
2023-12-14 23:36 | 0
2023-12-14 23:37 | 0
2023-12-14 23:38 | 0
2023-12-14 23:39 | 0
2023-12-14 23:40 | 0
2023-12-14 23:41 | 0
2023-12-14 23:42 | 0
2023-12-14 23:43 | 0
2023-12-14 23:44 | 0
2023-12-14 23:45 | 0
2023-12-14 23:46 | 0
2023-12-14 23:47 | 0
2023-12-14 23:48 | 0
2023-12-14 23:49 | 0
2023-12-14 23:50 | 0
2023-12-14 23:51 | 0
2023-12-14 23:52 | 0
2023-12-14 23:53 | 0
2023-12-14 23:54 | 0
2023-12-14 23:55 | 0
2023-12-14 23:56 | 0
2023-12-14 23:57 | 0
2023-12-14 23:58 | 0
2023-12-14 23:59 | 0
2023-12-15 | 0
2023-12-15 00:01 | 0
2023-12-15 00:02 | 0
2023-12-15 00:03 | 0
2023-12-15 00:04 | 0
2023-12-15 00:05 | 0
2023-12-15 00:06 | 0
2023-12-15 00:07 | 0
2023-12-15 00:08 | 0
2023-12-15 00:09 | 0
2023-12-15 00:10 | 0
2023-12-15 00:11 | 0
2023-12-15 00:12 | 0
2023-12-15 00:13 | 0
2023-12-15 00:14 | 0
2023-12-15 00:15 | 0
2023-12-15 00:16 | 0
2023-12-15 00:17 | 0
2023-12-15 00:18 | 0.0778
2023-12-15 00:19 | 0.0865
2023-12-15 00:20 | 0.0872
2023-12-15 00:21 | 0.0874
2023-12-15 00:22 | 0.0872
2023-12-15 00:23 | 0.0871
2023-12-15 00:24 | 0.0875
2023-12-15 00:25 | 0.0874
2023-12-15 00:26 | 0.0872
2023-12-15 00:27 | 0.087
2023-12-15 00:28 | 0.0876
2023-12-15 00:29 | 0.0876
2023-12-15 00:30 | 0.0144
2023-12-15 00:31 | 0
2023-12-15 00:32 | 0
2023-12-15 00:33 | 0
2023-12-15 00:34 | 0
2023-12-15 00:35 | 0
2023-12-15 00:36 | 0
2023-12-15 00:37 | 0
2023-12-15 00:38 | 0
2023-12-15 00:39 | 0
2023-12-15 00:40 | 0
2023-12-15 00:41 | 0
2023-12-15 00:42 | 0
2023-12-15 00:43 | 0
2023-12-15 00:44 | 0
2023-12-15 00:45 | 0
2023-12-15 00:46 | 0
2023-12-15 00:47 | 0
2023-12-15 00:48 | 0
2023-12-15 00:49 | 0
2023-12-15 00:50 | 0
2023-12-15 00:51 | 0
2023-12-15 00:52 | 0
2023-12-15 00:53 | 0
2023-12-15 00:54 | 0
2023-12-15 00:55 | 0
2023-12-15 00:56 | 0
2023-12-15 00:57 | 0
2023-12-15 00:58 | 0
2023-12-15 00:59 | 0
2023-12-15 01:00 | 0
2023-12-15 01:01 | 0
2023-12-15 01:02 | 0
2023-12-15 01:03 | 0
2023-12-15 01:04 | 0
2023-12-15 01:05 | 0
2023-12-15 01:06 | 0
2023-12-15 01:07 | 0
2023-12-15 01:08 | 0
2023-12-15 01:09 | 0
2023-12-15 01:10 | 0
2023-12-15 01:11 | 0
2023-12-15 01:12 | 0
2023-12-15 01:13 | 0
2023-12-15 01:14 | 0
2023-12-15 01:15 | 0
2023-12-15 01:16 | 0
2023-12-15 01:17 | 0
2023-12-15 01:18 | 0.0859
2023-12-15 01:19 | 0.086
2023-12-15 01:20 | 0.0869
2023-12-15 01:21 | 0.0866
2023-12-15 01:22 | 0.0867
2023-12-15 01:23 | 0.0869
2023-12-15 01:24 | 0.0872
2023-12-15 01:25 | 0.0869
2023-12-15 01:26 | 0.0872
2023-12-15 01:27 | 0.0872
2023-12-15 01:28 | 0.0871
2023-12-15 01:29 | 0.0873
2023-12-15 01:30 | 0.005
2023-12-15 01:31 | 0
2023-12-15 01:32 | 0
2023-12-15 01:33 | 0
2023-12-15 01:34 | 0
2023-12-15 01:35 | 0
2023-12-15 01:36 | 0
2023-12-15 01:37 | 0
2023-12-15 01:38 | 0
2023-12-15 01:39 | 0
2023-12-15 01:40 | 0
2023-12-15 01:41 | 0
2023-12-15 01:42 | 0
2023-12-15 01:43 | 0
2023-12-15 01:44 | 0
2023-12-15 01:45 | 0
2023-12-15 01:46 | 0
2023-12-15 01:47 | 0
2023-12-15 01:48 | 0
2023-12-15 01:49 | 0
2023-12-15 01:50 | 0
2023-12-15 01:51 | 0
2023-12-15 01:52 | 0
2023-12-15 01:53 | 0
2023-12-15 01:54 | 0
2023-12-15 01:55 | 0
2023-12-15 01:56 | 0
2023-12-15 01:57 | 0
2023-12-15 01:58 | 0
2023-12-15 01:59 | 0
2023-12-15 02:00 | 0
2023-12-15 02:01 | 0
2023-12-15 02:02 | 0
2023-12-15 02:03 | 0
2023-12-15 02:04 | 0
2023-12-15 02:05 | 0
2023-12-15 02:06 | 0
2023-12-15 02:07 | 0
2023-12-15 02:08 | 0
2023-12-15 02:09 | 0
2023-12-15 02:10 | 0
2023-12-15 02:11 | 0
2023-12-15 02:12 | 0
2023-12-15 02:13 | 0
2023-12-15 02:14 | 0
2023-12-15 02:15 | 0
2023-12-15 02:16 | 0
2023-12-15 02:17 | 0.0122
2023-12-15 02:18 | 0.0854
2023-12-15 02:19 | 0.0864
2023-12-15 02:20 | 0.0864
2023-12-15 02:21 | 0.0867
2023-12-15 02:22 | 0.0868
2023-12-15 02:23 | 0.087
2023-12-15 02:24 | 0.0871
2023-12-15 02:25 | 0.0871
2023-12-15 02:26 | 0.0869
2023-12-15 02:27 | 0.0868
2023-12-15 02:28 | 0.0874
2023-12-15 02:29 | 0.0798
2023-12-15 02:30 | 0
2023-12-15 02:31 | 0
2023-12-15 02:32 | 0
2023-12-15 02:33 | 0
2023-12-15 02:34 | 0
2023-12-15 02:35 | 0
2023-12-15 02:36 | 0
2023-12-15 02:37 | 0
2023-12-15 02:38 | 0
2023-12-15 02:39 | 0
2023-12-15 02:40 | 0
2023-12-15 02:41 | 0
2023-12-15 02:42 | 0
2023-12-15 02:43 | 0
2023-12-15 02:44 | 0
2023-12-15 02:45 | 0
2023-12-15 02:46 | 0
2023-12-15 02:47 | 0
2023-12-15 02:48 | 0
2023-12-15 02:49 | 0
2023-12-15 02:50 | 0
2023-12-15 02:51 | 0
2023-12-15 02:52 | 0
2023-12-15 02:53 | 0
2023-12-15 02:54 | 0
2023-12-15 02:55 | 0
2023-12-15 02:56 | 0
2023-12-15 02:57 | 0
2023-12-15 02:58 | 0
2023-12-15 02:59 | 0
2023-12-15 03:00 | 0
2023-12-15 03:01 | 0
2023-12-15 03:02 | 0
2023-12-15 03:03 | 0
2023-12-15 03:04 | 0
2023-12-15 03:05 | 0
2023-12-15 03:06 | 0
2023-12-15 03:07 | 0
2023-12-15 03:08 | 0
2023-12-15 03:09 | 0
2023-12-15 03:10 | 0
2023-12-15 03:11 | 0
2023-12-15 03:12 | 0
2023-12-15 03:13 | 0
2023-12-15 03:14 | 0
2023-12-15 03:15 | 0
2023-12-15 03:16 | 0
2023-12-15 03:17 | 0.0274
2023-12-15 03:18 | 0.0859
2023-12-15 03:19 | 0.0865
2023-12-15 03:20 | 0.0867
2023-12-15 03:21 | 0.0868
2023-12-15 03:22 | 0.0869
2023-12-15 03:23 | 0.0866
2023-12-15 03:24 | 0.087
2023-12-15 03:25 | 0.087
2023-12-15 03:26 | 0.0871
2023-12-15 03:27 | 0.0868
2023-12-15 03:28 | 0.0869
2023-12-15 03:29 | 0.0624
2023-12-15 03:30 | 0
2023-12-15 03:31 | 0
2023-12-15 03:32 | 0
2023-12-15 03:33 | 0
2023-12-15 03:34 | 0
2023-12-15 03:35 | 0
2023-12-15 03:36 | 0
2023-12-15 03:37 | 0
2023-12-15 03:38 | 0
2023-12-15 03:39 | 0
2023-12-15 03:40 | 0
2023-12-15 03:41 | 0
2023-12-15 03:42 | 0
2023-12-15 03:43 | 0
2023-12-15 03:44 | 0
2023-12-15 03:45 | 0
2023-12-15 03:46 | 0
2023-12-15 03:47 | 0
2023-12-15 03:48 | 0
2023-12-15 03:49 | 0
2023-12-15 03:50 | 0
2023-12-15 03:51 | 0
2023-12-15 03:52 | 0
2023-12-15 03:53 | 0
2023-12-15 03:54 | 0
2023-12-15 03:55 | 0
2023-12-15 03:56 | 0
2023-12-15 03:57 | 0
2023-12-15 03:58 | 0
2023-12-15 03:59 | 0
2023-12-15 04:00 | 0
2023-12-15 04:01 | 0
2023-12-15 04:02 | 0
2023-12-15 04:03 | 0
2023-12-15 04:04 | 0
2023-12-15 04:05 | 0
2023-12-15 04:06 | 0
2023-12-15 04:07 | 0
2023-12-15 04:08 | 0
2023-12-15 04:09 | 0
2023-12-15 04:10 | 0
2023-12-15 04:11 | 0
2023-12-15 04:12 | 0
2023-12-15 04:13 | 0
2023-12-15 04:14 | 0
2023-12-15 04:15 | 0
2023-12-15 04:16 | 0
2023-12-15 04:17 | 0.0474
2023-12-15 04:18 | 0.0858
2023-12-15 04:19 | 0.086
2023-12-15 04:20 | 0.0856
2023-12-15 04:21 | 0.086
2023-12-15 04:22 | 0.0863
2023-12-15 04:23 | 0.0867
2023-12-15 04:24 | 0.0869
2023-12-15 04:25 | 0.087
2023-12-15 04:26 | 0.087
2023-12-15 04:27 | 0.0867
2023-12-15 04:28 | 0.0868
2023-12-15 04:29 | 0.0433
2023-12-15 04:30 | 0
2023-12-15 04:31 | 0
2023-12-15 04:32 | 0
2023-12-15 04:33 | 0
2023-12-15 04:34 | 0
2023-12-15 04:35 | 0
2023-12-15 04:36 | 0
2023-12-15 04:37 | 0
2023-12-15 04:38 | 0
2023-12-15 04:39 | 0
2023-12-15 04:40 | 0
2023-12-15 04:41 | 0
2023-12-15 04:42 | 0
2023-12-15 04:43 | 0
2023-12-15 04:44 | 0
2023-12-15 04:45 | 0
2023-12-15 04:46 | 0
2023-12-15 04:47 | 0
2023-12-15 04:48 | 0
2023-12-15 04:49 | 0
2023-12-15 04:50 | 0
2023-12-15 04:51 | 0
2023-12-15 04:52 | 0
2023-12-15 04:53 | 0
2023-12-15 04:54 | 0
2023-12-15 04:55 | 0
2023-12-15 04:56 | 0
2023-12-15 04:57 | 0
2023-12-15 04:58 | 0
2023-12-15 04:59 | 0
2023-12-15 05:00 | 0
2023-12-15 05:01 | 0
2023-12-15 05:02 | 0
2023-12-15 05:03 | 0
2023-12-15 05:04 | 0
2023-12-15 05:05 | 0
2023-12-15 05:06 | 0
2023-12-15 05:07 | 0
2023-12-15 05:08 | 0
2023-12-15 05:09 | 0
2023-12-15 05:10 | 0
2023-12-15 05:11 | 0
2023-12-15 05:12 | 0
2023-12-15 05:13 | 0
2023-12-15 05:14 | 0
2023-12-15 05:15 | 0
2023-12-15 05:16 | 0
2023-12-15 05:17 | 0.0676
2023-12-15 05:18 | 0.0859
2023-12-15 05:19 | 0.0862
2023-12-15 05:20 | 0.0863
2023-12-15 05:21 | 0.0865
2023-12-15 05:22 | 0.0869
2023-12-15 05:23 | 0.0868
2023-12-15 05:24 | 0.0867
2023-12-15 05:25 | 0.0868
2023-12-15 05:26 | 0.0868
2023-12-15 05:27 | 0.0871
2023-12-15 05:28 | 0.0867
2023-12-15 05:29 | 0.0202
2023-12-15 05:30 | 0
2023-12-15 05:31 | 0
2023-12-15 05:32 | 0
2023-12-15 05:33 | 0
2023-12-15 05:34 | 0
2023-12-15 05:35 | 0
2023-12-15 05:36 | 0
2023-12-15 05:37 | 0
2023-12-15 05:38 | 0
2023-12-15 05:39 | 0
2023-12-15 05:40 | 0
2023-12-15 05:41 | 0
2023-12-15 05:42 | 0
2023-12-15 05:43 | 0
2023-12-15 05:44 | 0
2023-12-15 05:45 | 0
2023-12-15 05:46 | 0
2023-12-15 05:47 | 0
2023-12-15 05:48 | 0
2023-12-15 05:49 | 0
2023-12-15 05:50 | 0
2023-12-15 05:51 | 0
2023-12-15 05:52 | 0
2023-12-15 05:53 | 0
2023-12-15 05:54 | 0
2023-12-15 05:55 | 0
2023-12-15 05:56 | 0
2023-12-15 05:57 | 0
2023-12-15 05:58 | 0
2023-12-15 05:59 | 0
2023-12-15 06:00 | 0
2023-12-15 06:01 | 0
2023-12-15 06:02 | 0
2023-12-15 06:03 | 0
2023-12-15 06:04 | 0
2023-12-15 06:05 | 0
2023-12-15 06:06 | 0
2023-12-15 06:07 | 0
2023-12-15 06:08 | 0
2023-12-15 06:09 | 0
2023-12-15 06:10 | 0
2023-12-15 06:11 | 0
2023-12-15 06:12 | 0
2023-12-15 06:13 | 0
2023-12-15 06:14 | 0
2023-12-15 06:15 | 0
2023-12-15 06:16 | 0.0007
2023-12-15 06:17 | 0.0921
2023-12-15 06:18 | 0.0866
2023-12-15 06:19 | 0.0869
2023-12-15 06:20 | 0.0863
2023-12-15 06:21 | 0.0866
2023-12-15 06:22 | 0.0867
2023-12-15 06:23 | 0.0866
2023-12-15 06:24 | 0.0868
2023-12-15 06:25 | 0.0868
2023-12-15 06:26 | 0.087
2023-12-15 06:27 | 0.0868
2023-12-15 06:28 | 0.0837
2023-12-15 06:29 | 0
2023-12-15 06:30 | 0
2023-12-15 06:31 | 0
2023-12-15 06:32 | 0
2023-12-15 06:33 | 0
2023-12-15 06:34 | 0
2023-12-15 06:35 | 0
2023-12-15 06:36 | 0
2023-12-15 06:37 | 0
2023-12-15 06:38 | 0
2023-12-15 06:39 | 0
2023-12-15 06:40 | 0
2023-12-15 06:41 | 0
2023-12-15 06:42 | 0
2023-12-15 06:43 | 0
2023-12-15 06:44 | 0
2023-12-15 06:45 | 0
2023-12-15 06:46 | 0
2023-12-15 06:47 | 0
2023-12-15 06:48 | 0
2023-12-15 06:49 | 0
2023-12-15 06:50 | 0
2023-12-15 06:51 | 0
2023-12-15 06:52 | 0
2023-12-15 06:53 | 0
2023-12-15 06:54 | 0
2023-12-15 06:55 | 0
2023-12-15 06:56 | 0
2023-12-15 06:57 | 0
2023-12-15 06:58 | 0
2023-12-15 06:59 | 0
2023-12-15 07:00 | 0
2023-12-15 07:01 | 0
2023-12-15 07:02 | 0
2023-12-15 07:03 | 0
2023-12-15 07:04 | 0
2023-12-15 07:05 | 0
2023-12-15 07:06 | 0
2023-12-15 07:07 | 0
2023-12-15 07:08 | 0
2023-12-15 07:09 | 0
2023-12-15 07:10 | 0
2023-12-15 07:11 | 0
2023-12-15 07:12 | 0
2023-12-15 07:13 | 0
2023-12-15 07:14 | 0
2023-12-15 07:15 | 0
2023-12-15 07:16 | 0.0225
2023-12-15 07:17 | 0.0855
2023-12-15 07:18 | 0.0858
2023-12-15 07:19 | 0.0855
2023-12-15 07:20 | 0.0858
2023-12-15 07:21 | 0.0856
2023-12-15 07:22 | 0.0857
2023-12-15 07:23 | 0.0857
2023-12-15 07:24 | 0.0859
2023-12-15 07:25 | 0.0856
2023-12-15 07:26 | 0.0861
2023-12-15 07:27 | 0.0857
2023-12-15 07:28 | 0.0705
2023-12-15 07:29 | 0
2023-12-15 07:30 | 0
2023-12-15 07:31 | 0
2023-12-15 07:32 | 0
2023-12-15 07:33 | 0
2023-12-15 07:34 | 0
2023-12-15 07:35 | 0
2023-12-15 07:36 | 0
2023-12-15 07:37 | 0
2023-12-15 07:38 | 0
2023-12-15 07:39 | 0
2023-12-15 07:40 | 0
2023-12-15 07:41 | 0
2023-12-15 07:42 | 0
2023-12-15 07:43 | 0
2023-12-15 07:44 | 0
2023-12-15 07:45 | 0
2023-12-15 07:46 | 0
2023-12-15 07:47 | 0
2023-12-15 07:48 | 0
2023-12-15 07:49 | 0
2023-12-15 07:50 | 0
2023-12-15 07:51 | 0
2023-12-15 07:52 | 0
2023-12-15 07:53 | 0
2023-12-15 07:54 | 0
2023-12-15 07:55 | 0
2023-12-15 07:56 | 0
2023-12-15 07:57 | 0
2023-12-15 07:58 | 0
2023-12-15 07:59 | 0
2023-12-15 08:00 | 0
2023-12-15 08:01 | 0
2023-12-15 08:02 | 0
2023-12-15 08:03 | 0
2023-12-15 08:04 | 0
2023-12-15 08:05 | 0
2023-12-15 08:06 | 0
2023-12-15 08:07 | 0
2023-12-15 08:08 | 0
2023-12-15 08:09 | 0
2023-12-15 08:10 | 0
2023-12-15 08:11 | 0
2023-12-15 08:12 | 0
2023-12-15 08:13 | 0
2023-12-15 08:14 | 0
2023-12-15 08:15 | 0
2023-12-15 08:16 | 0.0246
2023-12-15 08:17 | 0.086
2023-12-15 08:18 | 0.0857
2023-12-15 08:19 | 0.0861
2023-12-15 08:20 | 0.0858
2023-12-15 08:21 | 0.086
2023-12-15 08:22 | 0.0859
2023-12-15 08:23 | 0.086
2023-12-15 08:24 | 0.0862
2023-12-15 08:25 | 0.0863
2023-12-15 08:26 | 0.0863
2023-12-15 08:27 | 0.0863
2023-12-15 08:28 | 0.0699
2023-12-15 08:29 | 0
2023-12-15 08:30 | 0
2023-12-15 08:31 | 0
2023-12-15 08:32 | 0
2023-12-15 08:33 | 0
2023-12-15 08:34 | 0
2023-12-15 08:35 | 0
2023-12-15 08:36 | 0
2023-12-15 08:37 | 0
2023-12-15 08:38 | 0
2023-12-15 08:39 | 0
2023-12-15 08:40 | 0
2023-12-15 08:41 | 0
2023-12-15 08:42 | 0
2023-12-15 08:43 | 0
2023-12-15 08:44 | 0
2023-12-15 08:45 | 0
2023-12-15 08:46 | 0
2023-12-15 08:47 | 0
2023-12-15 08:48 | 0
2023-12-15 08:49 | 0
2023-12-15 08:50 | 0
2023-12-15 08:51 | 0
2023-12-15 08:52 | 0
2023-12-15 08:53 | 0
2023-12-15 08:54 | 0
2023-12-15 08:55 | 0
2023-12-15 08:56 | 0
2023-12-15 08:57 | 0
2023-12-15 08:58 | 0
2023-12-15 08:59 | 0
2023-12-15 09:00 | 0
2023-12-15 09:01 | 0
2023-12-15 09:02 | 0
2023-12-15 09:03 | 0
2023-12-15 09:04 | 0
2023-12-15 09:05 | 0
2023-12-15 09:06 | 0
2023-12-15 09:07 | 0
2023-12-15 09:08 | 0
2023-12-15 09:09 | 0
2023-12-15 09:10 | 0
2023-12-15 09:11 | 0
2023-12-15 09:12 | 0
2023-12-15 09:13 | 0
2023-12-15 09:14 | 0
2023-12-15 09:15 | 0
2023-12-15 09:16 | 0.0159
2023-12-15 09:17 | 0.0857
2023-12-15 09:18 | 0.0858
2023-12-15 09:19 | 0.0855
2023-12-15 09:20 | 0.0857
2023-12-15 09:21 | 0.0857
2023-12-15 09:22 | 0.0856
2023-12-15 09:23 | 0.0861
2023-12-15 09:24 | 0.0859
2023-12-15 09:25 | 0.086
2023-12-15 09:26 | 0.0864
2023-12-15 09:27 | 0.0859
2023-12-15 09:28 | 0.0814
2023-12-15 09:29 | 0
2023-12-15 09:30 | 0
2023-12-15 09:31 | 0
2023-12-15 09:32 | 0
2023-12-15 09:33 | 0
2023-12-15 09:34 | 0
2023-12-15 09:35 | 0
2023-12-15 09:36 | 0
2023-12-15 09:37 | 0
2023-12-15 09:38 | 0
2023-12-15 09:39 | 0
2023-12-15 09:40 | 0
2023-12-15 09:41 | 0
2023-12-15 09:42 | 0
2023-12-15 09:43 | 0
2023-12-15 09:44 | 0
2023-12-15 09:45 | 0
2023-12-15 09:46 | 0
2023-12-15 09:47 | 0
2023-12-15 09:48 | 0
2023-12-15 09:49 | 0
2023-12-15 09:50 | 0
2023-12-15 09:51 | 0
2023-12-15 09:52 | 0
2023-12-15 09:53 | 0
2023-12-15 09:54 | 0
2023-12-15 09:55 | 0
2023-12-15 09:56 | 0
2023-12-15 09:57 | 0
2023-12-15 09:58 | 0
2023-12-15 09:59 | 0
2023-12-15 10:00 | 0
2023-12-15 10:01 | 0
2023-12-15 10:02 | 0
2023-12-15 10:03 | 0
2023-12-15 10:04 | 0
2023-12-15 10:05 | 0
2023-12-15 10:06 | 0
2023-12-15 10:07 | 0
2023-12-15 10:08 | 0
2023-12-15 10:09 | 0
2023-12-15 10:10 | 0
2023-12-15 10:11 | 0
2023-12-15 10:12 | 0
2023-12-15 10:13 | 0
2023-12-15 10:14 | 0
2023-12-15 10:15 | 0
2023-12-15 10:16 | 0
2023-12-15 10:17 | 0.0772
2023-12-15 10:18 | 0.085
2023-12-15 10:19 | 0.0852
2023-12-15 10:20 | 0.0853
2023-12-15 10:21 | 0.0853
2023-12-15 10:22 | 0.085
2023-12-15 10:23 | 0.0852
2023-12-15 10:24 | 0.0858
2023-12-15 10:25 | 0.0861
2023-12-15 10:26 | 0.0856
2023-12-15 10:27 | 0.086
2023-12-15 10:28 | 0.086
2023-12-15 10:29 | 0.0205
2023-12-15 10:30 | 0
2023-12-15 10:31 | 0
2023-12-15 10:32 | 0
2023-12-15 10:33 | 0
2023-12-15 10:34 | 0
2023-12-15 10:35 | 0
2023-12-15 10:36 | 0
2023-12-15 10:37 | 0
2023-12-15 10:38 | 0
2023-12-15 10:39 | 0
2023-12-15 10:40 | 0
2023-12-15 10:41 | 0
2023-12-15 10:42 | 0
2023-12-15 10:43 | 0
2023-12-15 10:44 | 0
2023-12-15 10:45 | 0
2023-12-15 10:46 | 0
2023-12-15 10:47 | 0
2023-12-15 10:48 | 0
2023-12-15 10:49 | 0
2023-12-15 10:50 | 0
2023-12-15 10:51 | 0
2023-12-15 10:52 | 0
2023-12-15 10:53 | 0
2023-12-15 10:54 | 0
2023-12-15 10:55 | 0
2023-12-15 10:56 | 0
2023-12-15 10:57 | 0
2023-12-15 10:58 | 0
2023-12-15 10:59 | 0
2023-12-15 11:00 | 0
2023-12-15 11:01 | 0
2023-12-15 11:02 | 0
2023-12-15 11:03 | 0
2023-12-15 11:04 | 0
2023-12-15 11:05 | 0
2023-12-15 11:06 | 0
2023-12-15 11:07 | 0
2023-12-15 11:08 | 0
2023-12-15 11:09 | 0
2023-12-15 11:10 | 0
2023-12-15 11:11 | 0
2023-12-15 11:12 | 0
2023-12-15 11:13 | 0
2023-12-15 11:14 | 0
2023-12-15 11:15 | 0
2023-12-15 11:16 | 0
2023-12-15 11:17 | 0.0506
2023-12-15 11:18 | 0.0853
2023-12-15 11:19 | 0.0854
2023-12-15 11:20 | 0.0856
2023-12-15 11:21 | 0.0858
2023-12-15 11:22 | 0.0859
2023-12-15 11:23 | 0.086
2023-12-15 11:24 | 0.0857
2023-12-15 11:25 | 0.0857
2023-12-15 11:26 | 0.0861
2023-12-15 11:27 | 0.0855
2023-12-15 11:28 | 0.0863
2023-12-15 11:29 | 0.0471
2023-12-15 11:30 | 0
2023-12-15 11:31 | 0
2023-12-15 11:32 | 0
2023-12-15 11:33 | 0
2023-12-15 11:34 | 0
2023-12-15 11:35 | 0
2023-12-15 11:36 | 0
2023-12-15 11:37 | 0
2023-12-15 11:38 | 0
2023-12-15 11:39 | 0
2023-12-15 11:40 | 0
2023-12-15 11:41 | 0
2023-12-15 11:42 | 0
2023-12-15 11:43 | 0
2023-12-15 11:44 | 0
2023-12-15 11:45 | 0
2023-12-15 11:46 | 0
2023-12-15 11:47 | 0
2023-12-15 11:48 | 0
2023-12-15 11:49 | 0
2023-12-15 11:50 | 0
2023-12-15 11:51 | 0
2023-12-15 11:52 | 0
2023-12-15 11:53 | 0
2023-12-15 11:54 | 0
2023-12-15 11:55 | 0
2023-12-15 11:56 | 0
2023-12-15 11:57 | 0
2023-12-15 11:58 | 0
2023-12-15 11:59 | 0
2023-12-15 12:00 | 0
2023-12-15 12:01 | 0
2023-12-15 12:02 | 0
2023-12-15 12:03 | 0
2023-12-15 12:04 | 0
2023-12-15 12:05 | 0
2023-12-15 12:06 | 0
2023-12-15 12:07 | 0
2023-12-15 12:08 | 0
2023-12-15 12:09 | 0
2023-12-15 12:10 | 0
2023-12-15 12:11 | 0
2023-12-15 12:12 | 0
2023-12-15 12:13 | 0
2023-12-15 12:14 | 0
2023-12-15 12:15 | 0
2023-12-15 12:16 | 0
2023-12-15 12:17 | 0.0247
2023-12-15 12:18 | 0.0854
2023-12-15 12:19 | 0.0854
2023-12-15 12:20 | 0.0853
2023-12-15 12:21 | 0.0854
2023-12-15 12:22 | 0.086
2023-12-15 12:23 | 0.0861
2023-12-15 12:24 | 0.0858
2023-12-15 12:25 | 0.0863
2023-12-15 12:26 | 0.0861
2023-12-15 12:27 | 0.086
2023-12-15 12:28 | 0.0857
2023-12-15 12:29 | 0.0745
2023-12-15 12:30 | 0
2023-12-15 12:31 | 0
2023-12-15 12:32 | 0
2023-12-15 12:33 | 0
2023-12-15 12:34 | 0
2023-12-15 12:35 | 0
2023-12-15 12:36 | 0
2023-12-15 12:37 | 0
2023-12-15 12:38 | 0
2023-12-15 12:39 | 0
2023-12-15 12:40 | 0
2023-12-15 12:41 | 0
2023-12-15 12:42 | 0
2023-12-15 12:43 | 0
2023-12-15 12:44 | 0
2023-12-15 12:45 | 0
2023-12-15 12:46 | 0
2023-12-15 12:47 | 0
2023-12-15 12:48 | 0
2023-12-15 12:49 | 0
2023-12-15 12:50 | 0
2023-12-15 12:51 | 0
2023-12-15 12:52 | 0
2023-12-15 12:53 | 0
2023-12-15 12:54 | 0
2023-12-15 12:55 | 0
2023-12-15 12:56 | 0
2023-12-15 12:57 | 0
2023-12-15 12:58 | 0
2023-12-15 12:59 | 0
2023-12-15 13:00 | 0
2023-12-15 13:01 | 0
2023-12-15 13:02 | 0
2023-12-15 13:03 | 0
2023-12-15 13:04 | 0
2023-12-15 13:05 | 0
2023-12-15 13:06 | 0
2023-12-15 13:07 | 0
2023-12-15 13:08 | 0
2023-12-15 13:09 | 0
2023-12-15 13:10 | 0
2023-12-15 13:11 | 0
2023-12-15 13:12 | 0
2023-12-15 13:13 | 0
2023-12-15 13:14 | 0
2023-12-15 13:15 | 0
2023-12-15 13:16 | 0
2023-12-15 13:17 | 0
2023-12-15 13:18 | 0.0808
2023-12-15 13:19 | 0.0848
2023-12-15 13:20 | 0.0852
2023-12-15 13:21 | 0.0846
2023-12-15 13:22 | 0.085
2023-12-15 13:23 | 0.0856
2023-12-15 13:24 | 0.0858
2023-12-15 13:25 | 0.086
2023-12-15 13:26 | 0.0856
2023-12-15 13:27 | 0.0862
2023-12-15 13:28 | 0.0857
2023-12-15 13:29 | 0.0854
2023-12-15 13:30 | 0.0162
2023-12-15 13:31 | 0
2023-12-15 13:32 | 0
2023-12-15 13:33 | 0
2023-12-15 13:34 | 0
2023-12-15 13:35 | 0
2023-12-15 13:36 | 0
2023-12-15 13:37 | 0
2023-12-15 13:38 | 0
2023-12-15 13:39 | 0
2023-12-15 13:40 | 0
2023-12-15 13:41 | 0
2023-12-15 13:42 | 0
2023-12-15 13:43 | 0
2023-12-15 13:44 | 0
2023-12-15 13:45 | 0
2023-12-15 13:46 | 0
2023-12-15 13:47 | 0
2023-12-15 13:48 | 0
2023-12-15 13:49 | 0
2023-12-15 13:50 | 0
2023-12-15 13:51 | 0
2023-12-15 13:52 | 0
2023-12-15 13:53 | 0
2023-12-15 13:54 | 0
2023-12-15 13:55 | 0
2023-12-15 13:56 | 0
2023-12-15 13:57 | 0
2023-12-15 13:58 | 0
2023-12-15 13:59 | 0
2023-12-15 14:00 | 0
2023-12-15 14:01 | 0
2023-12-15 14:02 | 0
2023-12-15 14:03 | 0
2023-12-15 14:04 | 0
2023-12-15 14:05 | 0
2023-12-15 14:06 | 0
2023-12-15 14:07 | 0
2023-12-15 14:08 | 0
2023-12-15 14:09 | 0
2023-12-15 14:10 | 0
2023-12-15 14:11 | 0
2023-12-15 14:12 | 0
2023-12-15 14:13 | 0
2023-12-15 14:14 | 0
2023-12-15 14:15 | 0
2023-12-15 14:16 | 0
2023-12-15 14:17 | 0
2023-12-15 14:18 | 0.0491
2023-12-15 14:19 | 0.0845
2023-12-15 14:20 | 0.085
2023-12-15 14:21 | 0.085
2023-12-15 14:22 | 0.0851
2023-12-15 14:23 | 0.0847
2023-12-15 14:24 | 0.0851
2023-12-15 14:25 | 0.0858
2023-12-15 14:26 | 0.0859
2023-12-15 14:27 | 0.0858
2023-12-15 14:28 | 0.0855
2023-12-15 14:29 | 0.0853
2023-12-15 14:30 | 0.0493
2023-12-15 14:31 | 0
2023-12-15 14:32 | 0
2023-12-15 14:33 | 0
2023-12-15 14:34 | 0
2023-12-15 14:35 | 0
2023-12-15 14:36 | 0
2023-12-15 14:37 | 0
2023-12-15 14:38 | 0
2023-12-15 14:39 | 0
2023-12-15 14:40 | 0
2023-12-15 14:41 | 0
2023-12-15 14:42 | 0
2023-12-15 14:43 | 0
2023-12-15 14:44 | 0
2023-12-15 14:45 | 0
2023-12-15 14:46 | 0
2023-12-15 14:47 | 0
2023-12-15 14:48 | 0
2023-12-15 14:49 | 0
2023-12-15 14:50 | 0
2023-12-15 14:51 | 0
2023-12-15 14:52 | 0
2023-12-15 14:53 | 0
2023-12-15 14:54 | 0
2023-12-15 14:55 | 0
2023-12-15 14:56 | 0
2023-12-15 14:57 | 0
2023-12-15 14:58 | 0
2023-12-15 14:59 | 0
2023-12-15 15:00 | 0
2023-12-15 15:01 | 0
2023-12-15 15:02 | 0
2023-12-15 15:03 | 0
2023-12-15 15:04 | 0
2023-12-15 15:05 | 0
2023-12-15 15:06 | 0
2023-12-15 15:07 | 0
2023-12-15 15:08 | 0
2023-12-15 15:09 | 0
2023-12-15 15:10 | 0
2023-12-15 15:11 | 0
2023-12-15 15:12 | 0
2023-12-15 15:13 | 0
2023-12-15 15:14 | 0
2023-12-15 15:15 | 0
2023-12-15 15:16 | 0
2023-12-15 15:17 | 0
2023-12-15 15:18 | 0.016
2023-12-15 15:19 | 0.0845
2023-12-15 15:20 | 0.0844
2023-12-15 15:21 | 0.0846
2023-12-15 15:22 | 0.085
2023-12-15 15:23 | 0.0854
2023-12-15 15:24 | 0.0849
2023-12-15 15:25 | 0.0855
2023-12-15 15:26 | 0.0853
2023-12-15 15:27 | 0.0853
2023-12-15 15:28 | 0.0855
2023-12-15 15:29 | 0.0849
2023-12-15 15:30 | 0.083
2023-12-15 15:31 | 0
2023-12-15 15:32 | 0
2023-12-15 15:33 | 0
2023-12-15 15:34 | 0
2023-12-15 15:35 | 0
2023-12-15 15:36 | 0
2023-12-15 15:37 | 0
2023-12-15 15:38 | 0
2023-12-15 15:39 | 0
2023-12-15 15:40 | 0
2023-12-15 15:41 | 0
2023-12-15 15:42 | 0
2023-12-15 15:43 | 0
2023-12-15 15:44 | 0
2023-12-15 15:45 | 0
2023-12-15 15:46 | 0
2023-12-15 15:47 | 0
2023-12-15 15:48 | 0
2023-12-15 15:49 | 0
2023-12-15 15:50 | 0
2023-12-15 15:51 | 0
2023-12-15 15:52 | 0
2023-12-15 15:53 | 0
2023-12-15 15:54 | 0
2023-12-15 15:55 | 0
2023-12-15 15:56 | 0
2023-12-15 15:57 | 0
2023-12-15 15:58 | 0
2023-12-15 15:59 | 0
2023-12-15 16:00 | 0
2023-12-15 16:01 | 0
2023-12-15 16:02 | 0
2023-12-15 16:03 | 0
2023-12-15 16:04 | 0
2023-12-15 16:05 | 0
2023-12-15 16:06 | 0
2023-12-15 16:07 | 0
2023-12-15 16:08 | 0
2023-12-15 16:09 | 0
2023-12-15 16:10 | 0
2023-12-15 16:11 | 0
2023-12-15 16:12 | 0
2023-12-15 16:13 | 0
2023-12-15 16:14 | 0
2023-12-15 16:15 | 0
2023-12-15 16:16 | 0
2023-12-15 16:17 | 0
2023-12-15 16:18 | 0
2023-12-15 16:19 | 0.0666
2023-12-15 16:20 | 0.0847
2023-12-15 16:21 | 0.0849
2023-12-15 16:22 | 0.0848
2023-12-15 16:23 | 0.0848
2023-12-15 16:24 | 0.0849
2023-12-15 16:25 | 0.0849
2023-12-15 16:26 | 0.0849
2023-12-15 16:27 | 0.085
2023-12-15 16:28 | 0.0849
2023-12-15 16:29 | 0.0851
2023-12-15 16:30 | 0.0849
2023-12-15 16:31 | 0.0306
2023-12-15 16:32 | 0
2023-12-15 16:33 | 0
2023-12-15 16:34 | 0
2023-12-15 16:35 | 0
2023-12-15 16:36 | 0
2023-12-15 16:37 | 0
2023-12-15 16:38 | 0
2023-12-15 16:39 | 0
2023-12-15 16:40 | 0
2023-12-15 16:41 | 0
2023-12-15 16:42 | 0
2023-12-15 16:43 | 0
2023-12-15 16:44 | 0
2023-12-15 16:45 | 0
2023-12-15 16:46 | 0
2023-12-15 16:47 | 0
2023-12-15 16:48 | 0
2023-12-15 16:49 | 0
2023-12-15 16:50 | 0
2023-12-15 16:51 | 0
2023-12-15 16:52 | 0
2023-12-15 16:53 | 0
2023-12-15 16:54 | 0
2023-12-15 16:55 | 0
2023-12-15 16:56 | 0
2023-12-15 16:57 | 0
2023-12-15 16:58 | 0
2023-12-15 16:59 | 0
2023-12-15 17:00 | 0
2023-12-15 17:01 | 0
2023-12-15 17:02 | 0
2023-12-15 17:03 | 0
2023-12-15 17:04 | 0
2023-12-15 17:05 | 0
2023-12-15 17:06 | 0.0418
2023-12-15 17:07 | 0.0849
2023-12-15 17:08 | 0.0853
2023-12-15 17:09 | 0.0849
2023-12-15 17:10 | 0.0853
2023-12-15 17:11 | 0.0852
2023-12-15 17:12 | 0.0851
2023-12-15 17:13 | 0.0852
2023-12-15 17:14 | 0.0852
2023-12-15 17:15 | 0.0854
2023-12-15 17:16 | 0.0851
2023-12-15 17:17 | 0.0855
2023-12-15 17:18 | 0.0854
2023-12-15 17:19 | 0.0853
2023-12-15 17:20 | 0.0854
2023-12-15 17:21 | 0.0853
2023-12-15 17:22 | 0.0856
2023-12-15 17:23 | 0.0853
2023-12-15 17:24 | 0.0853
2023-12-15 17:25 | 0.0854
2023-12-15 17:26 | 0.0856
2023-12-15 17:27 | 0.0856
2023-12-15 17:28 | 0.0856
2023-12-15 17:29 | 0.0852
2023-12-15 17:30 | 0.0854
2023-12-15 17:31 | 0.0617
2023-12-15 17:32 | 0
2023-12-15 17:33 | 0
2023-12-15 17:34 | 0
2023-12-15 17:35 | 0
2023-12-15 17:36 | 0
2023-12-15 17:37 | 0
2023-12-15 17:38 | 0
2023-12-15 17:39 | 0
2023-12-15 17:40 | 0
2023-12-15 17:41 | 0
2023-12-15 17:42 | 0
2023-12-15 17:43 | 0
2023-12-15 17:44 | 0
2023-12-15 17:45 | 0
2023-12-15 17:46 | 0
2023-12-15 17:47 | 0
2023-12-15 17:48 | 0
2023-12-15 17:49 | 0
2023-12-15 17:50 | 0
2023-12-15 17:51 | 0
2023-12-15 17:52 | 0
2023-12-15 17:53 | 0
2023-12-15 17:54 | 0
2023-12-15 17:55 | 0
2023-12-15 17:56 | 0
2023-12-15 17:57 | 0
2023-12-15 17:58 | 0
2023-12-15 17:59 | 0
2023-12-15 18:00 | 0
2023-12-15 18:01 | 0
2023-12-15 18:02 | 0
2023-12-15 18:03 | 0
2023-12-15 18:04 | 0
2023-12-15 18:05 | 0
2023-12-15 18:06 | 0
2023-12-15 18:07 | 0
2023-12-15 18:08 | 0
2023-12-15 18:09 | 0
2023-12-15 18:10 | 0
2023-12-15 18:11 | 0
2023-12-15 18:12 | 0
2023-12-15 18:13 | 0
2023-12-15 18:14 | 0
2023-12-15 18:15 | 0.0743
2023-12-15 18:16 | 0.0856
2023-12-15 18:17 | 0.0857
2023-12-15 18:18 | 0.0862
2023-12-15 18:19 | 0.086
2023-12-15 18:20 | 0.0859
2023-12-15 18:21 | 0.0857
2023-12-15 18:22 | 0.0859
2023-12-15 18:23 | 0.0858
2023-12-15 18:24 | 0.0857
2023-12-15 18:25 | 0.0857
2023-12-15 18:26 | 0.0857
2023-12-15 18:27 | 0.0856
2023-12-15 18:28 | 0.0851
2023-12-15 18:29 | 0.0849
2023-12-15 18:30 | 0.085
2023-12-15 18:31 | 0.0853
2023-12-15 18:32 | 0.0854
2023-12-15 18:33 | 0.0853
2023-12-15 18:34 | 0.0852
2023-12-15 18:35 | 0.0287
2023-12-15 18:36 | 0
2023-12-15 18:37 | 0
2023-12-15 18:38 | 0
2023-12-15 18:39 | 0
2023-12-15 18:40 | 0
2023-12-15 18:41 | 0
2023-12-15 18:42 | 0
2023-12-15 18:43 | 0
2023-12-15 18:44 | 0
2023-12-15 18:45 | 0
2023-12-15 18:46 | 0
2023-12-15 18:47 | 0
2023-12-15 18:48 | 0
2023-12-15 18:49 | 0
2023-12-15 18:50 | 0
2023-12-15 18:51 | 0
2023-12-15 18:52 | 0
2023-12-15 18:53 | 0
2023-12-15 18:54 | 0
2023-12-15 18:55 | 0
2023-12-15 18:56 | 0
2023-12-15 18:57 | 0
2023-12-15 18:58 | 0
2023-12-15 18:59 | 0
2023-12-15 19:00 | 0
2023-12-15 19:01 | 0
2023-12-15 19:02 | 0
2023-12-15 19:03 | 0
2023-12-15 19:04 | 0
2023-12-15 19:05 | 0
2023-12-15 19:06 | 0
2023-12-15 19:07 | 0
2023-12-15 19:08 | 0
2023-12-15 19:09 | 0
2023-12-15 19:10 | 0
2023-12-15 19:11 | 0
2023-12-15 19:12 | 0
2023-12-15 19:13 | 0
2023-12-15 19:14 | 0
2023-12-15 19:15 | 0
2023-12-15 19:16 | 0
2023-12-15 19:17 | 0
2023-12-15 19:18 | 0
2023-12-15 19:19 | 0
2023-12-15 19:20 | 0.0642
2023-12-15 19:21 | 0.0854
2023-12-15 19:22 | 0.0858
2023-12-15 19:23 | 0.086
2023-12-15 19:24 | 0.0861
2023-12-15 19:25 | 0.0862
2023-12-15 19:26 | 0.0861
2023-12-15 19:27 | 0.0862
2023-12-15 19:28 | 0.0863
2023-12-15 19:29 | 0.0866
2023-12-15 19:30 | 0.0861
2023-12-15 19:31 | 0.0861
2023-12-15 19:32 | 0.0341
2023-12-15 19:33 | 0
2023-12-15 19:34 | 0
2023-12-15 19:35 | 0
2023-12-15 19:36 | 0
2023-12-15 19:37 | 0
2023-12-15 19:38 | 0
2023-12-15 19:39 | 0
2023-12-15 19:40 | 0
2023-12-15 19:41 | 0
2023-12-15 19:42 | 0
2023-12-15 19:43 | 0
2023-12-15 19:44 | 0
2023-12-15 19:45 | 0
2023-12-15 19:46 | 0
2023-12-15 19:47 | 0
2023-12-15 19:48 | 0
2023-12-15 19:49 | 0
2023-12-15 19:50 | 0
2023-12-15 19:51 | 0
2023-12-15 19:52 | 0
2023-12-15 19:53 | 0
2023-12-15 19:54 | 0
2023-12-15 19:55 | 0
2023-12-15 19:56 | 0
2023-12-15 19:57 | 0
2023-12-15 19:58 | 0
2023-12-15 19:59 | 0
2023-12-15 20:00 | 0
2023-12-15 20:01 | 0
2023-12-15 20:02 | 0
2023-12-15 20:03 | 0
2023-12-15 20:04 | 0
2023-12-15 20:05 | 0
2023-12-15 20:06 | 0
2023-12-15 20:07 | 0
2023-12-15 20:08 | 0
2023-12-15 20:09 | 0
2023-12-15 20:10 | 0
2023-12-15 20:11 | 0
2023-12-15 20:12 | 0
2023-12-15 20:13 | 0
2023-12-15 20:14 | 0
2023-12-15 20:15 | 0
2023-12-15 20:16 | 0
2023-12-15 20:17 | 0
2023-12-15 20:18 | 0
2023-12-15 20:19 | 0
2023-12-15 20:20 | 0.0351
2023-12-15 20:21 | 0.0851
2023-12-15 20:22 | 0.0857
2023-12-15 20:23 | 0.0858
2023-12-15 20:24 | 0.0859
2023-12-15 20:25 | 0.0861
2023-12-15 20:26 | 0.0859
2023-12-15 20:27 | 0.086
2023-12-15 20:28 | 0.0861
2023-12-15 20:29 | 0.0861
2023-12-15 20:30 | 0.0861
2023-12-15 20:31 | 0.0864
2023-12-15 20:32 | 0.0633
2023-12-15 20:33 | 0
2023-12-15 20:34 | 0
2023-12-15 20:35 | 0
2023-12-15 20:36 | 0
2023-12-15 20:37 | 0
2023-12-15 20:38 | 0
2023-12-15 20:39 | 0
2023-12-15 20:40 | 0
2023-12-15 20:41 | 0
2023-12-15 20:42 | 0
2023-12-15 20:43 | 0
2023-12-15 20:44 | 0
2023-12-15 20:45 | 0
2023-12-15 20:46 | 0
2023-12-15 20:47 | 0
2023-12-15 20:48 | 0
2023-12-15 20:49 | 0
2023-12-15 20:50 | 0
2023-12-15 20:51 | 0
2023-12-15 20:52 | 0
2023-12-15 20:53 | 0
2023-12-15 20:54 | 0
2023-12-15 20:55 | 0
2023-12-15 20:56 | 0
2023-12-15 20:57 | 0
2023-12-15 20:58 | 0
2023-12-15 20:59 | 0
2023-12-15 21:00 | 0
2023-12-15 21:01 | 0
2023-12-15 21:02 | 0
2023-12-15 21:03 | 0
2023-12-15 21:04 | 0
2023-12-15 21:05 | 0
2023-12-15 21:06 | 0
2023-12-15 21:07 | 0
2023-12-15 21:08 | 0
2023-12-15 21:09 | 0
2023-12-15 21:10 | 0
2023-12-15 21:11 | 0
2023-12-15 21:12 | 0
2023-12-15 21:13 | 0
2023-12-15 21:14 | 0
2023-12-15 21:15 | 0
2023-12-15 21:16 | 0
2023-12-15 21:17 | 0
2023-12-15 21:18 | 0
2023-12-15 21:19 | 0
2023-12-15 21:20 | 0.0031
2023-12-15 21:21 | 0.0888
2023-12-15 21:22 | 0.0854
2023-12-15 21:23 | 0.0858
2023-12-15 21:24 | 0.0863
2023-12-15 21:25 | 0.0864
2023-12-15 21:26 | 0.0865
2023-12-15 21:27 | 0.0864
2023-12-15 21:28 | 0.0864
2023-12-15 21:29 | 0.0866
2023-12-15 21:30 | 0.0867
2023-12-15 21:31 | 0.0866
2023-12-15 21:32 | 0.0869
2023-12-15 21:33 | 0.0057
2023-12-15 21:34 | 0
2023-12-15 21:35 | 0
2023-12-15 21:36 | 0
2023-12-15 21:37 | 0
2023-12-15 21:38 | 0
2023-12-15 21:39 | 0
2023-12-15 21:40 | 0
2023-12-15 21:41 | 0
2023-12-15 21:42 | 0
2023-12-15 21:43 | 0
2023-12-15 21:44 | 0
2023-12-15 21:45 | 0
2023-12-15 21:46 | 0
2023-12-15 21:47 | 0
2023-12-15 21:48 | 0
2023-12-15 21:49 | 0
2023-12-15 21:50 | 0.0238
2023-12-15 21:51 | 0.0866
2023-12-15 21:52 | 0.0873
2023-12-15 21:53 | 0.0873
2023-12-15 21:54 | 0.0875
2023-12-15 21:55 | 0.0875
2023-12-15 21:56 | 0.0875
2023-12-15 21:57 | 0.0874
2023-12-15 21:58 | 0.0872
2023-12-15 21:59 | 0.0871
2023-12-15 22:00 | 0.0869
2023-12-15 22:01 | 0.0871
2023-12-15 22:02 | 0.087
2023-12-15 22:03 | 0.0872
2023-12-15 22:04 | 0.0871
2023-12-15 22:05 | 0.0872
2023-12-15 22:06 | 0.0873
2023-12-15 22:07 | 0.0873
2023-12-15 22:08 | 0.0873
2023-12-15 22:09 | 0.0874
2023-12-15 22:10 | 0.0873
2023-12-15 22:11 | 0.0873
2023-12-15 22:12 | 0.0875
2023-12-15 22:13 | 0.0874
2023-12-15 22:14 | 0.0874
2023-12-15 22:15 | 0.0874
2023-12-15 22:16 | 0.0874
2023-12-15 22:17 | 0.0874
2023-12-15 22:18 | 0.0877
2023-12-15 22:19 | 0.0877
2023-12-15 22:20 | 0.0875
2023-12-15 22:21 | 0.0877
2023-12-15 22:22 | 0.0875
2023-12-15 22:23 | 0.0876
2023-12-15 22:24 | 0.0875
2023-12-15 22:25 | 0.0874
2023-12-15 22:26 | 0.0875
2023-12-15 22:27 | 0.0874
2023-12-15 22:28 | 0.0873
2023-12-15 22:29 | 0.0876
2023-12-15 22:30 | 0.0875
2023-12-15 22:31 | 0.0877
2023-12-15 22:32 | 0.0877
2023-12-15 22:33 | 0.0876
2023-12-15 22:34 | 0.0878
2023-12-15 22:35 | 0.0877
2023-12-15 22:36 | 0.0879
2023-12-15 22:37 | 0.0877
2023-12-15 22:38 | 0.0879
2023-12-15 22:39 | 0.0879
2023-12-15 22:40 | 0.088
2023-12-15 22:41 | 0.0879
2023-12-15 22:42 | 0.088
2023-12-15 22:43 | 0.0879
2023-12-15 22:44 | 0.0877
2023-12-15 22:45 | 0.0126
2023-12-15 22:46 | 0
2023-12-15 22:47 | 0
2023-12-15 22:48 | 0
2023-12-15 22:49 | 0
2023-12-15 22:50 | 0
2023-12-15 22:51 | 0.0784
2023-12-15 22:52 | 0.0874
2023-12-15 22:53 | 0.0875
2023-12-15 22:54 | 0.0875
2023-12-15 22:55 | 0.0874
2023-12-15 22:56 | 0.0877
2023-12-15 22:57 | 0.0876
2023-12-15 22:58 | 0.0878
2023-12-15 22:59 | 0.0877
2023-12-15 23:00 | 0.0878
2023-12-15 23:01 | 0.0878
2023-12-15 23:02 | 0.0878
2023-12-15 23:03 | 0.0877
2023-12-15 23:04 | 0.0878
2023-12-15 23:05 | 0.0877
2023-12-15 23:06 | 0.0876
2023-12-15 23:07 | 0.0876
2023-12-15 23:08 | 0.0879
2023-12-15 23:09 | 0.088
2023-12-15 23:10 | 0.088
2023-12-15 23:11 | 0.0878
2023-12-15 23:12 | 0.088
2023-12-15 23:13 | 0.0878
2023-12-15 23:14 | 0.0879
2023-12-15 23:15 | 0.088
2023-12-15 23:16 | 0.0879
2023-12-15 23:17 | 0.0878
2023-12-15 23:18 | 0.0878
2023-12-15 23:19 | 0.0878
2023-12-15 23:20 | 0.088
2023-12-15 23:21 | 0.088
2023-12-15 23:22 | 0.0884
2023-12-15 23:23 | 0.0882
2023-12-15 23:24 | 0.0882
2023-12-15 23:25 | 0.0882
2023-12-15 23:26 | 0.0882
2023-12-15 23:27 | 0.0882
2023-12-15 23:28 | 0.088
2023-12-15 23:29 | 0.0881
2023-12-15 23:30 | 0.088
2023-12-15 23:31 | 0.0881
2023-12-15 23:32 | 0.0877
2023-12-15 23:33 | 0.0876
2023-12-15 23:34 | 0.0877
2023-12-15 23:35 | 0.0874
2023-12-15 23:36 | 0.0875
2023-12-15 23:37 | 0.0876
2023-12-15 23:38 | 0.0876
2023-12-15 23:39 | 0.0878
2023-12-15 23:40 | 0.0878
2023-12-15 23:41 | 0.0876
2023-12-15 23:42 | 0.0878
2023-12-15 23:43 | 0.0877
2023-12-15 23:44 | 0.0877
2023-12-15 23:45 | 0.0392
2023-12-15 23:46 | 0
2023-12-15 23:47 | 0
2023-12-15 23:48 | 0
2023-12-15 23:49 | 0
2023-12-15 23:50 | 0
2023-12-15 23:51 | 0.0524
2023-12-15 23:52 | 0.0871
2023-12-15 23:53 | 0.0871
2023-12-15 23:54 | 0.0874
2023-12-15 23:55 | 0.0873
2023-12-15 23:56 | 0.0875
2023-12-15 23:57 | 0.0875
2023-12-15 23:58 | 0.0874
2023-12-15 23:59 | 0.0874
2023-12-16 | 0.0875
2023-12-16 00:01 | 0.0874
2023-12-16 00:02 | 0.0877
2023-12-16 00:03 | 0.0878
2023-12-16 00:04 | 0.0877
2023-12-16 00:05 | 0.0877
2023-12-16 00:06 | 0.0877
2023-12-16 00:07 | 0.0878
2023-12-16 00:08 | 0.0879
2023-12-16 00:09 | 0.0879
2023-12-16 00:10 | 0.088
2023-12-16 00:11 | 0.0876
2023-12-16 00:12 | 0.0876
2023-12-16 00:13 | 0.0879
2023-12-16 00:14 | 0.0877
2023-12-16 00:15 | 0.0877
2023-12-16 00:16 | 0.0876
2023-12-16 00:17 | 0.0875
2023-12-16 00:18 | 0.0876
2023-12-16 00:19 | 0.0875
2023-12-16 00:20 | 0.0874
2023-12-16 00:21 | 0.0875
2023-12-16 00:22 | 0.0875
2023-12-16 00:23 | 0.0876
2023-12-16 00:24 | 0.0872
2023-12-16 00:25 | 0.0868
2023-12-16 00:26 | 0.0869
2023-12-16 00:27 | 0.0873
2023-12-16 00:28 | 0.0874
2023-12-16 00:29 | 0.0874
2023-12-16 00:30 | 0.0874
2023-12-16 00:31 | 0.0875
2023-12-16 00:32 | 0.0875
2023-12-16 00:33 | 0.0874
2023-12-16 00:34 | 0.0874
2023-12-16 00:35 | 0.0875
2023-12-16 00:36 | 0.0876
2023-12-16 00:37 | 0.0876
2023-12-16 00:38 | 0.0875
2023-12-16 00:39 | 0.0875
2023-12-16 00:40 | 0.0877
2023-12-16 00:41 | 0.0876
2023-12-16 00:42 | 0.0876
2023-12-16 00:43 | 0.0877
2023-12-16 00:44 | 0.088
2023-12-16 00:45 | 0.058
2023-12-16 00:46 | 0
2023-12-16 00:47 | 0
2023-12-16 00:48 | 0
2023-12-16 00:49 | 0
2023-12-16 00:50 | 0
2023-12-16 00:51 | 0.0352
2023-12-16 00:52 | 0.0876
2023-12-16 00:53 | 0.0877
2023-12-16 00:54 | 0.0876
2023-12-16 00:55 | 0.0877
2023-12-16 00:56 | 0.0878
2023-12-16 00:57 | 0.0878
2023-12-16 00:58 | 0.0881
2023-12-16 00:59 | 0.0879
2023-12-16 01:00 | 0.0879
2023-12-16 01:01 | 0.0878
2023-12-16 01:02 | 0.0878
2023-12-16 01:03 | 0.0879
2023-12-16 01:04 | 0.0879
2023-12-16 01:05 | 0.0881
2023-12-16 01:06 | 0.088
2023-12-16 01:07 | 0.0881
2023-12-16 01:08 | 0.088
2023-12-16 01:09 | 0.0883
2023-12-16 01:10 | 0.0884
2023-12-16 01:11 | 0.0883
2023-12-16 01:12 | 0.0885
2023-12-16 01:13 | 0.0884
2023-12-16 01:14 | 0.0886
2023-12-16 01:15 | 0.0883
2023-12-16 01:16 | 0.0884
2023-12-16 01:17 | 0.0883
2023-12-16 01:18 | 0.0884
2023-12-16 01:19 | 0.0882
2023-12-16 01:20 | 0.0882
2023-12-16 01:21 | 0.0882
2023-12-16 01:22 | 0.0882
2023-12-16 01:23 | 0.088
2023-12-16 01:24 | 0.0879
2023-12-16 01:25 | 0.0883
2023-12-16 01:26 | 0.0884
2023-12-16 01:27 | 0.0882
2023-12-16 01:28 | 0.0882
2023-12-16 01:29 | 0.0881
2023-12-16 01:30 | 0.0884
2023-12-16 01:31 | 0.0884
2023-12-16 01:32 | 0.0883
2023-12-16 01:33 | 0.0883
2023-12-16 01:34 | 0.0885
2023-12-16 01:35 | 0.0885
2023-12-16 01:36 | 0.0885
2023-12-16 01:37 | 0.0884
2023-12-16 01:38 | 0.0884
2023-12-16 01:39 | 0.0884
2023-12-16 01:40 | 0.0884
2023-12-16 01:41 | 0.0885
2023-12-16 01:42 | 0.0884
2023-12-16 01:43 | 0.0884
2023-12-16 01:44 | 0.0884
2023-12-16 01:45 | 0.0737
2023-12-16 01:46 | 0
2023-12-16 01:47 | 0
2023-12-16 01:48 | 0
2023-12-16 01:49 | 0
2023-12-16 01:50 | 0
2023-12-16 01:51 | 0.0199
2023-12-16 01:52 | 0.0885
2023-12-16 01:53 | 0.0883
2023-12-16 01:54 | 0.0883
2023-12-16 01:55 | 0.0883
2023-12-16 01:56 | 0.0884
2023-12-16 01:57 | 0.0883
2023-12-16 01:58 | 0.0884
2023-12-16 01:59 | 0.0886
2023-12-16 02:00 | 0.0884
2023-12-16 02:01 | 0.0884
2023-12-16 02:02 | 0.0885
2023-12-16 02:03 | 0.0884
2023-12-16 02:04 | 0.0884
2023-12-16 02:05 | 0.0884
2023-12-16 02:06 | 0.0885
2023-12-16 02:07 | 0.0884
2023-12-16 02:08 | 0.0885
2023-12-16 02:09 | 0.0886
2023-12-16 02:10 | 0.0886
2023-12-16 02:11 | 0.0885
2023-12-16 02:12 | 0.0883
2023-12-16 02:13 | 0.0885
2023-12-16 02:14 | 0.0886
2023-12-16 02:15 | 0.0884
2023-12-16 02:16 | 0.0885
2023-12-16 02:17 | 0.0886
2023-12-16 02:18 | 0.0884
2023-12-16 02:19 | 0.0883
2023-12-16 02:20 | 0.0885
2023-12-16 02:21 | 0.0888
2023-12-16 02:22 | 0.0887
2023-12-16 02:23 | 0.0886
2023-12-16 02:24 | 0.0885
2023-12-16 02:25 | 0.0885
2023-12-16 02:26 | 0.0886
2023-12-16 02:27 | 0.0884
2023-12-16 02:28 | 0.0885
2023-12-16 02:29 | 0.0883
2023-12-16 02:30 | 0.0885
2023-12-16 02:31 | 0.0885
2023-12-16 02:32 | 0.0884
2023-12-16 02:33 | 0.0887
2023-12-16 02:34 | 0.0885
2023-12-16 02:35 | 0.0885
2023-12-16 02:36 | 0.0886
2023-12-16 02:37 | 0.0887
2023-12-16 02:38 | 0.0886
2023-12-16 02:39 | 0.0887
2023-12-16 02:40 | 0.0886
2023-12-16 02:41 | 0.0886
2023-12-16 02:42 | 0.0886
2023-12-16 02:43 | 0.0886
2023-12-16 02:44 | 0.0888
2023-12-16 02:45 | 0.0847
2023-12-16 02:46 | 0
2023-12-16 02:47 | 0
2023-12-16 02:48 | 0
2023-12-16 02:49 | 0
2023-12-16 02:50 | 0
2023-12-16 02:51 | 0.0093
2023-12-16 02:52 | 0.0886
2023-12-16 02:53 | 0.0883
2023-12-16 02:54 | 0.0881
2023-12-16 02:55 | 0.0884
2023-12-16 02:56 | 0.0885
2023-12-16 02:57 | 0.0888
2023-12-16 02:58 | 0.0886
2023-12-16 02:59 | 0.0886
2023-12-16 03:00 | 0.0884
2023-12-16 03:01 | 0.0886
2023-12-16 03:02 | 0.0886
2023-12-16 03:03 | 0.0888
2023-12-16 03:04 | 0.0888
2023-12-16 03:05 | 0.0886
2023-12-16 03:06 | 0.0886
2023-12-16 03:07 | 0.0885
2023-12-16 03:08 | 0.0887
2023-12-16 03:09 | 0.0886
2023-12-16 03:10 | 0.0885
2023-12-16 03:11 | 0.0886
2023-12-16 03:12 | 0.0888
2023-12-16 03:13 | 0.0887
2023-12-16 03:14 | 0.0885
2023-12-16 03:15 | 0.0885
2023-12-16 03:16 | 0.0885
2023-12-16 03:17 | 0.0885
2023-12-16 03:18 | 0.0886
2023-12-16 03:19 | 0.0886
2023-12-16 03:20 | 0.0889
2023-12-16 03:21 | 0.0887
2023-12-16 03:22 | 0.0885
2023-12-16 03:23 | 0.0885
2023-12-16 03:24 | 0.0885
2023-12-16 03:25 | 0.0885
2023-12-16 03:26 | 0.0886
2023-12-16 03:27 | 0.0885
2023-12-16 03:28 | 0.0886
2023-12-16 03:29 | 0.0886
2023-12-16 03:30 | 0.0886
2023-12-16 03:31 | 0.0884
2023-12-16 03:32 | 0.0886
2023-12-16 03:33 | 0.0882
2023-12-16 03:34 | 0.0884
2023-12-16 03:35 | 0.0885
2023-12-16 03:36 | 0.0883
2023-12-16 03:37 | 0.0885
2023-12-16 03:38 | 0.0887
2023-12-16 03:39 | 0.0884
2023-12-16 03:40 | 0.0884
2023-12-16 03:41 | 0.0886
2023-12-16 03:42 | 0.0885
2023-12-16 03:43 | 0.0885
2023-12-16 03:44 | 0.0886
2023-12-16 03:45 | 0.0887
2023-12-16 03:46 | 0.0032
2023-12-16 03:47 | 0
2023-12-16 03:48 | 0
2023-12-16 03:49 | 0
2023-12-16 03:50 | 0
2023-12-16 03:51 | 0
2023-12-16 03:52 | 0.0911
2023-12-16 03:53 | 0.0883
2023-12-16 03:54 | 0.0885
2023-12-16 03:55 | 0.0884
2023-12-16 03:56 | 0.0884
2023-12-16 03:57 | 0.0885
2023-12-16 03:58 | 0.0886
2023-12-16 03:59 | 0.0885
2023-12-16 04:00 | 0.0885
2023-12-16 04:01 | 0.0885
2023-12-16 04:02 | 0.0887
2023-12-16 04:03 | 0.0888
2023-12-16 04:04 | 0.0888
2023-12-16 04:05 | 0.0888
2023-12-16 04:06 | 0.0889
2023-12-16 04:07 | 0.0889
2023-12-16 04:08 | 0.0889
2023-12-16 04:09 | 0.089
2023-12-16 04:10 | 0.0889
2023-12-16 04:11 | 0.0887
2023-12-16 04:12 | 0.0888
2023-12-16 04:13 | 0.0887
2023-12-16 04:14 | 0.0889
2023-12-16 04:15 | 0.0889
2023-12-16 04:16 | 0.0887
2023-12-16 04:17 | 0.0887
2023-12-16 04:18 | 0.0886
2023-12-16 04:19 | 0.0888
2023-12-16 04:20 | 0.0888
2023-12-16 04:21 | 0.0888
2023-12-16 04:22 | 0.089
2023-12-16 04:23 | 0.0891
2023-12-16 04:24 | 0.089
2023-12-16 04:25 | 0.0889
2023-12-16 04:26 | 0.089
2023-12-16 04:27 | 0.089
2023-12-16 04:28 | 0.0888
2023-12-16 04:29 | 0.0889
2023-12-16 04:30 | 0.0888
2023-12-16 04:31 | 0.0888
2023-12-16 04:32 | 0.0889
2023-12-16 04:33 | 0.0889
2023-12-16 04:34 | 0.0889
2023-12-16 04:35 | 0.0888
2023-12-16 04:36 | 0.0887
2023-12-16 04:37 | 0.0887
2023-12-16 04:38 | 0.0887
2023-12-16 04:39 | 0.0887
2023-12-16 04:40 | 0.0886
2023-12-16 04:41 | 0.0888
2023-12-16 04:42 | 0.0885
2023-12-16 04:43 | 0.0888
2023-12-16 04:44 | 0.0889
2023-12-16 04:45 | 0.0887
2023-12-16 04:46 | 0.007
2023-12-16 04:47 | 0
2023-12-16 04:48 | 0
2023-12-16 04:49 | 0
2023-12-16 04:50 | 0
2023-12-16 04:51 | 0
2023-12-16 04:52 | 0.0879
2023-12-16 04:53 | 0.0886
2023-12-16 04:54 | 0.0885
2023-12-16 04:55 | 0.0885
2023-12-16 04:56 | 0.0883
2023-12-16 04:57 | 0.0889
2023-12-16 04:58 | 0.0885
2023-12-16 04:59 | 0.0886
2023-12-16 05:00 | 0.0885
2023-12-16 05:01 | 0.0884
2023-12-16 05:02 | 0.0885
2023-12-16 05:03 | 0.0888
2023-12-16 05:04 | 0.0886
2023-12-16 05:05 | 0.0887
2023-12-16 05:06 | 0.0887
2023-12-16 05:07 | 0.0887
2023-12-16 05:08 | 0.0889
2023-12-16 05:09 | 0.0886
2023-12-16 05:10 | 0.0888
2023-12-16 05:11 | 0.0889
2023-12-16 05:12 | 0.0889
2023-12-16 05:13 | 0.0889
2023-12-16 05:14 | 0.0889
2023-12-16 05:15 | 0.0889
2023-12-16 05:16 | 0.089
2023-12-16 05:17 | 0.089
2023-12-16 05:18 | 0.0889
2023-12-16 05:19 | 0.0891
2023-12-16 05:20 | 0.0892
2023-12-16 05:21 | 0.089
2023-12-16 05:22 | 0.0891
2023-12-16 05:23 | 0.0891
2023-12-16 05:24 | 0.0892
2023-12-16 05:25 | 0.0893
2023-12-16 05:26 | 0.0893
2023-12-16 05:27 | 0.0893
2023-12-16 05:28 | 0.0891
2023-12-16 05:29 | 0.089
2023-12-16 05:30 | 0.0891
2023-12-16 05:31 | 0.089
2023-12-16 05:32 | 0.0893
2023-12-16 05:33 | 0.0894
2023-12-16 05:34 | 0.0891
2023-12-16 05:35 | 0.0892
2023-12-16 05:36 | 0.0891
2023-12-16 05:37 | 0.0887
2023-12-16 05:38 | 0.0886
2023-12-16 05:39 | 0.0888
2023-12-16 05:40 | 0.0889
2023-12-16 05:41 | 0.0888
2023-12-16 05:42 | 0.0888
2023-12-16 05:43 | 0.0885
2023-12-16 05:44 | 0.0887
2023-12-16 05:45 | 0.0885
2023-12-16 05:46 | 0.0077
2023-12-16 05:47 | 0
2023-12-16 05:48 | 0
2023-12-16 05:49 | 0
2023-12-16 05:50 | 0
2023-12-16 05:51 | 0
2023-12-16 05:52 | 0.0884
2023-12-16 05:53 | 0.0885
2023-12-16 05:54 | 0.0885
2023-12-16 05:55 | 0.0884
2023-12-16 05:56 | 0.0883
2023-12-16 05:57 | 0.0881
2023-12-16 05:58 | 0.0883
2023-12-16 05:59 | 0.088
2023-12-16 06:00 | 0.0882
2023-12-16 06:01 | 0.088
2023-12-16 06:02 | 0.0878
2023-12-16 06:03 | 0.0879
2023-12-16 06:04 | 0.0878
2023-12-16 06:05 | 0.0879
2023-12-16 06:06 | 0.0879
2023-12-16 06:07 | 0.088
2023-12-16 06:08 | 0.088
2023-12-16 06:09 | 0.0881
2023-12-16 06:10 | 0.0882
2023-12-16 06:11 | 0.0881
2023-12-16 06:12 | 0.0881
2023-12-16 06:13 | 0.088
2023-12-16 06:14 | 0.088
2023-12-16 06:15 | 0.0878
2023-12-16 06:16 | 0.0879
2023-12-16 06:17 | 0.0879
2023-12-16 06:18 | 0.0877
2023-12-16 06:19 | 0.0879
2023-12-16 06:20 | 0.0881
2023-12-16 06:21 | 0.0876
2023-12-16 06:22 | 0.0878
2023-12-16 06:23 | 0.0878
2023-12-16 06:24 | 0.0876
2023-12-16 06:25 | 0.0876
2023-12-16 06:26 | 0.0877
2023-12-16 06:27 | 0.0879
2023-12-16 06:28 | 0.0881
2023-12-16 06:29 | 0.0882
2023-12-16 06:30 | 0.0882
2023-12-16 06:31 | 0.0882
2023-12-16 06:32 | 0.0881
2023-12-16 06:33 | 0.0881
2023-12-16 06:34 | 0.0883
2023-12-16 06:35 | 0.0883
2023-12-16 06:36 | 0.0883
2023-12-16 06:37 | 0.0882
2023-12-16 06:38 | 0.0883
2023-12-16 06:39 | 0.0878
2023-12-16 06:40 | 0.0879
2023-12-16 06:41 | 0.0878
2023-12-16 06:42 | 0.087
2023-12-16 06:43 | 0.0868
2023-12-16 06:44 | 0.0867
2023-12-16 06:45 | 0.0868
2023-12-16 06:46 | 0.0078
2023-12-16 06:47 | 0
2023-12-16 06:48 | 0
2023-12-16 06:49 | 0
2023-12-16 06:50 | 0
2023-12-16 06:51 | 0
2023-12-16 06:52 | 0.0848
2023-12-16 06:53 | 0.0864
2023-12-16 06:54 | 0.0864
2023-12-16 06:55 | 0.0871
2023-12-16 06:56 | 0.0865
2023-12-16 06:57 | 0.0875
2023-12-16 06:58 | 0.0876
2023-12-16 06:59 | 0.088
2023-12-16 07:00 | 0.0877
2023-12-16 07:01 | 0.0878
2023-12-16 07:02 | 0.0875
2023-12-16 07:03 | 0.0877
2023-12-16 07:04 | 0.0876
2023-12-16 07:05 | 0.0875
2023-12-16 07:06 | 0.0877
2023-12-16 07:07 | 0.0876
2023-12-16 07:08 | 0.0877
2023-12-16 07:09 | 0.0879
2023-12-16 07:10 | 0.0876
2023-12-16 07:11 | 0.0877
2023-12-16 07:12 | 0.0879
2023-12-16 07:13 | 0.0876
2023-12-16 07:14 | 0.0877
2023-12-16 07:15 | 0.0877
2023-12-16 07:16 | 0.0881
2023-12-16 07:17 | 0.088
2023-12-16 07:18 | 0.0878
2023-12-16 07:19 | 0.0883
2023-12-16 07:20 | 0.088
2023-12-16 07:21 | 0.0882
2023-12-16 07:22 | 0.088
2023-12-16 07:23 | 0.0881
2023-12-16 07:24 | 0.0882
2023-12-16 07:25 | 0.0878
2023-12-16 07:26 | 0.0877
2023-12-16 07:27 | 0.0879
2023-12-16 07:28 | 0.0881
2023-12-16 07:29 | 0.0876
2023-12-16 07:30 | 0.0874
2023-12-16 07:31 | 0.0873
2023-12-16 07:32 | 0.0873
2023-12-16 07:33 | 0.0875
2023-12-16 07:34 | 0.0875
2023-12-16 07:35 | 0.0875
2023-12-16 07:36 | 0.0876
2023-12-16 07:37 | 0.0876
2023-12-16 07:38 | 0.0874
2023-12-16 07:39 | 0.0876
2023-12-16 07:40 | 0.0876
2023-12-16 07:41 | 0.0877
2023-12-16 07:42 | 0.0878
2023-12-16 07:43 | 0.0881
2023-12-16 07:44 | 0.0882
2023-12-16 07:45 | 0.0881
2023-12-16 07:46 | 0.0187
2023-12-16 07:47 | 0
2023-12-16 07:48 | 0
2023-12-16 07:49 | 0
2023-12-16 07:50 | 0
2023-12-16 07:51 | 0
2023-12-16 07:52 | 0
2023-12-16 07:53 | 0
2023-12-16 07:54 | 0
2023-12-16 07:55 | 0
2023-12-16 07:56 | 0
2023-12-16 07:57 | 0
2023-12-16 07:58 | 0
2023-12-16 07:59 | 0
2023-12-16 08:00 | 0
2023-12-16 08:01 | 0
2023-12-16 08:02 | 0
2023-12-16 08:03 | 0
2023-12-16 08:04 | 0
2023-12-16 08:05 | 0.0899
2023-12-16 08:06 | 0.0872
2023-12-16 08:07 | 0.0872
2023-12-16 08:08 | 0.0872
2023-12-16 08:09 | 0.0872
2023-12-16 08:10 | 0.0875
2023-12-16 08:11 | 0.0875
2023-12-16 08:12 | 0.0872
2023-12-16 08:13 | 0.0872
2023-12-16 08:14 | 0.0871
2023-12-16 08:15 | 0.0873
2023-12-16 08:16 | 0.0879
2023-12-16 08:17 | 0.0875
2023-12-16 08:18 | 0.0876
2023-12-16 08:19 | 0.0877
2023-12-16 08:20 | 0.0876
2023-12-16 08:21 | 0.0873
2023-12-16 08:22 | 0.087
2023-12-16 08:23 | 0.0871
2023-12-16 08:24 | 0.0875
2023-12-16 08:25 | 0.0086
2023-12-16 08:26 | 0
2023-12-16 08:27 | 0
2023-12-16 08:28 | 0
2023-12-16 08:29 | 0
2023-12-16 08:30 | 0
2023-12-16 08:31 | 0
2023-12-16 08:32 | 0
2023-12-16 08:33 | 0
2023-12-16 08:34 | 0
2023-12-16 08:35 | 0
2023-12-16 08:36 | 0
2023-12-16 08:37 | 0
2023-12-16 08:38 | 0
2023-12-16 08:39 | 0
2023-12-16 08:40 | 0
2023-12-16 08:41 | 0
2023-12-16 08:42 | 0
2023-12-16 08:43 | 0
2023-12-16 08:44 | 0
2023-12-16 08:45 | 0
2023-12-16 08:46 | 0
2023-12-16 08:47 | 0
2023-12-16 08:48 | 0
2023-12-16 08:49 | 0
2023-12-16 08:50 | 0
2023-12-16 08:51 | 0
2023-12-16 08:52 | 0
2023-12-16 08:53 | 0
2023-12-16 08:54 | 0
2023-12-16 08:55 | 0
2023-12-16 08:56 | 0
2023-12-16 08:57 | 0
2023-12-16 08:58 | 0
2023-12-16 08:59 | 0
2023-12-16 09:00 | 0
2023-12-16 09:01 | 0
2023-12-16 09:02 | 0
2023-12-16 09:03 | 0
2023-12-16 09:04 | 0
2023-12-16 09:05 | 0
2023-12-16 09:06 | 0
2023-12-16 09:07 | 0
2023-12-16 09:08 | 0
2023-12-16 09:09 | 0
2023-12-16 09:10 | 0
2023-12-16 09:11 | 0
2023-12-16 09:12 | 0
2023-12-16 09:13 | 0
2023-12-16 09:14 | 0
2023-12-16 09:15 | 0
2023-12-16 09:16 | 0
2023-12-16 09:17 | 0
2023-12-16 09:18 | 0
2023-12-16 09:19 | 0
2023-12-16 09:20 | 0
2023-12-16 09:21 | 0
2023-12-16 09:22 | 0
2023-12-16 09:23 | 0
2023-12-16 09:24 | 0
2023-12-16 09:25 | 0
2023-12-16 09:26 | 0
2023-12-16 09:27 | 0
2023-12-16 09:28 | 0
2023-12-16 09:29 | 0
2023-12-16 09:30 | 0.0092
2023-12-16 09:31 | 0.0878
2023-12-16 09:32 | 0.0871
2023-12-16 09:33 | 0.0872
2023-12-16 09:34 | 0.0871
2023-12-16 09:35 | 0.0874
2023-12-16 09:36 | 0.0874
2023-12-16 09:37 | 0.0873
2023-12-16 09:38 | 0.0874
2023-12-16 09:39 | 0.0872
2023-12-16 09:40 | 0.0873
2023-12-16 09:41 | 0.0874
2023-12-16 09:42 | 0.0873
2023-12-16 09:43 | 0.0873
2023-12-16 09:44 | 0.0874
2023-12-16 09:45 | 0.0873
2023-12-16 09:46 | 0.0875
2023-12-16 09:47 | 0.0875
2023-12-16 09:48 | 0.0876
2023-12-16 09:49 | 0.0875
2023-12-16 09:50 | 0.0875
2023-12-16 09:51 | 0.0876
2023-12-16 09:52 | 0.0875
2023-12-16 09:53 | 0.0874
2023-12-16 09:54 | 0.0875
2023-12-16 09:55 | 0.0874
2023-12-16 09:56 | 0.0875
2023-12-16 09:57 | 0.0876
2023-12-16 09:58 | 0.088
2023-12-16 09:59 | 0.0875
2023-12-16 10:00 | 0.0876
2023-12-16 10:01 | 0.0876
2023-12-16 10:02 | 0.0875
2023-12-16 10:03 | 0.0877
2023-12-16 10:04 | 0.0876
2023-12-16 10:05 | 0.0875
2023-12-16 10:06 | 0.0875
2023-12-16 10:07 | 0.0878
2023-12-16 10:08 | 0.0875
2023-12-16 10:09 | 0.0875
2023-12-16 10:10 | 0.0876
2023-12-16 10:11 | 0.0875
2023-12-16 10:12 | 0.0877
2023-12-16 10:13 | 0.0876
2023-12-16 10:14 | 0.0874
2023-12-16 10:15 | 0.0875
2023-12-16 10:16 | 0.0872
2023-12-16 10:17 | 0.0872
2023-12-16 10:18 | 0.0872
2023-12-16 10:19 | 0.0873
2023-12-16 10:20 | 0.087
2023-12-16 10:21 | 0.0871
2023-12-16 10:22 | 0.0871
2023-12-16 10:23 | 0.0871
2023-12-16 10:24 | 0.0872
2023-12-16 10:25 | 0.0871
2023-12-16 10:26 | 0.0873
2023-12-16 10:27 | 0.0872
2023-12-16 10:28 | 0.0875
2023-12-16 10:29 | 0.0874
2023-12-16 10:30 | 0.0875
2023-12-16 10:31 | 0.0875
2023-12-16 10:32 | 0.0876
2023-12-16 10:33 | 0.0875
2023-12-16 10:34 | 0.0874
2023-12-16 10:35 | 0.0873
2023-12-16 10:36 | 0.0874
2023-12-16 10:37 | 0.0874
2023-12-16 10:38 | 0.0872
2023-12-16 10:39 | 0.0874
2023-12-16 10:40 | 0.0875
2023-12-16 10:41 | 0.0874
2023-12-16 10:42 | 0.0873
2023-12-16 10:43 | 0.0875
2023-12-16 10:44 | 0.0875
2023-12-16 10:45 | 0.0873
2023-12-16 10:46 | 0.0872
2023-12-16 10:47 | 0.0872
2023-12-16 10:48 | 0.0874
2023-12-16 10:49 | 0.0873
2023-12-16 10:50 | 0.0875
2023-12-16 10:51 | 0.0874
2023-12-16 10:52 | 0.087
2023-12-16 10:53 | 0.0875
2023-12-16 10:54 | 0.0874
2023-12-16 10:55 | 0.0872
2023-12-16 10:56 | 0.0819
2023-12-16 10:57 | 0.0233
2023-12-16 10:58 | 0
2023-12-16 10:59 | 0
2023-12-16 11:00 | 0
2023-12-16 11:01 | 0
2023-12-16 11:02 | 0
2023-12-16 11:03 | 0
2023-12-16 11:04 | 0
2023-12-16 11:05 | 0
2023-12-16 11:06 | 0
2023-12-16 11:07 | 0
2023-12-16 11:08 | 0
2023-12-16 11:09 | 0
2023-12-16 11:10 | 0
2023-12-16 11:11 | 0
2023-12-16 11:12 | 0
2023-12-16 11:13 | 0
2023-12-16 11:14 | 0
2023-12-16 11:15 | 0
2023-12-16 11:16 | 0
2023-12-16 11:17 | 0
2023-12-16 11:18 | 0
2023-12-16 11:19 | 0
2023-12-16 11:20 | 0
2023-12-16 11:21 | 0
2023-12-16 11:22 | 0.0275
2023-12-16 11:23 | 0.0866
2023-12-16 11:24 | 0.0865
2023-12-16 11:25 | 0.0868
2023-12-16 11:26 | 0.0869
2023-12-16 11:27 | 0.0871
2023-12-16 11:28 | 0.087
2023-12-16 11:29 | 0.0868
2023-12-16 11:30 | 0.0868
2023-12-16 11:31 | 0.0869
2023-12-16 11:32 | 0.0869
2023-12-16 11:33 | 0.0868
2023-12-16 11:34 | 0.0869
2023-12-16 11:35 | 0.087
2023-12-16 11:36 | 0.0868
2023-12-16 11:37 | 0.0867
2023-12-16 11:38 | 0.087
2023-12-16 11:39 | 0.087
2023-12-16 11:40 | 0.087
2023-12-16 11:41 | 0.087
2023-12-16 11:42 | 0.0871
2023-12-16 11:43 | 0.0871
2023-12-16 11:44 | 0.0871
2023-12-16 11:45 | 0.0872
2023-12-16 11:46 | 0.0869
2023-12-16 11:47 | 0.0857
2023-12-16 11:48 | 0.0856
2023-12-16 11:49 | 0.0858
2023-12-16 11:50 | 0.0863
2023-12-16 11:51 | 0.0855
2023-12-16 11:52 | 0.0864
2023-12-16 11:53 | 0.087
2023-12-16 11:54 | 0.0871
2023-12-16 11:55 | 0.087
2023-12-16 11:56 | 0.0873
2023-12-16 11:57 | 0.0873
2023-12-16 11:58 | 0.0871
2023-12-16 11:59 | 0.0871
2023-12-16 12:00 | 0.0868
2023-12-16 12:01 | 0.0873
2023-12-16 12:02 | 0.0869
2023-12-16 12:03 | 0.0871
2023-12-16 12:04 | 0.0873
2023-12-16 12:05 | 0.0871
2023-12-16 12:06 | 0.0872
2023-12-16 12:07 | 0.0876
2023-12-16 12:08 | 0.0875
2023-12-16 12:09 | 0.0874
2023-12-16 12:10 | 0.0874
2023-12-16 12:11 | 0.0873
2023-12-16 12:12 | 0.0871
2023-12-16 12:13 | 0.0873
2023-12-16 12:14 | 0.0874
2023-12-16 12:15 | 0.0874
2023-12-16 12:16 | 0.0874
2023-12-16 12:17 | 0.0875
2023-12-16 12:18 | 0.0873
2023-12-16 12:19 | 0.0874
2023-12-16 12:20 | 0.0872
2023-12-16 12:21 | 0.0877
2023-12-16 12:22 | 0.0876
2023-12-16 12:23 | 0.0874
2023-12-16 12:24 | 0.0875
2023-12-16 12:25 | 0.0877
2023-12-16 12:26 | 0.0877
2023-12-16 12:27 | 0.0875
2023-12-16 12:28 | 0.0874
2023-12-16 12:29 | 0.0873
2023-12-16 12:30 | 0.0874
2023-12-16 12:31 | 0.0874
2023-12-16 12:32 | 0.0874
2023-12-16 12:33 | 0.0873
2023-12-16 12:34 | 0.0875
2023-12-16 12:35 | 0.0876
2023-12-16 12:36 | 0.0873
2023-12-16 12:37 | 0.0874
2023-12-16 12:38 | 0.0872
2023-12-16 12:39 | 0.0874
2023-12-16 12:40 | 0.0873
2023-12-16 12:41 | 0.0873
2023-12-16 12:42 | 0.0875
2023-12-16 12:43 | 0.0876
2023-12-16 12:44 | 0.0876
2023-12-16 12:45 | 0.0871
2023-12-16 12:46 | 0.0872
2023-12-16 12:47 | 0.0873
2023-12-16 12:48 | 0.0635
2023-12-16 12:49 | 0
2023-12-16 12:50 | 0
2023-12-16 12:51 | 0
2023-12-16 12:52 | 0
2023-12-16 12:53 | 0
2023-12-16 12:54 | 0
2023-12-16 12:55 | 0
2023-12-16 12:56 | 0
2023-12-16 12:57 | 0
2023-12-16 12:58 | 0
2023-12-16 12:59 | 0
2023-12-16 13:00 | 0
2023-12-16 13:01 | 0
2023-12-16 13:02 | 0
2023-12-16 13:03 | 0
2023-12-16 13:04 | 0
2023-12-16 13:05 | 0
2023-12-16 13:06 | 0
2023-12-16 13:07 | 0
2023-12-16 13:08 | 0
2023-12-16 13:09 | 0
2023-12-16 13:10 | 0
2023-12-16 13:11 | 0
2023-12-16 13:12 | 0
2023-12-16 13:13 | 0
2023-12-16 13:14 | 0
2023-12-16 13:15 | 0
2023-12-16 13:16 | 0
2023-12-16 13:17 | 0
2023-12-16 13:18 | 0
2023-12-16 13:19 | 0
2023-12-16 13:20 | 0
2023-12-16 13:21 | 0
2023-12-16 13:22 | 0
2023-12-16 13:23 | 0
2023-12-16 13:24 | 0
2023-12-16 13:25 | 0
2023-12-16 13:26 | 0
2023-12-16 13:27 | 0
2023-12-16 13:28 | 0
2023-12-16 13:29 | 0
2023-12-16 13:30 | 0
2023-12-16 13:31 | 0
2023-12-16 13:32 | 0
2023-12-16 13:33 | 0
2023-12-16 13:34 | 0
2023-12-16 13:35 | 0
2023-12-16 13:36 | 0
2023-12-16 13:37 | 0
2023-12-16 13:38 | 0
2023-12-16 13:39 | 0
2023-12-16 13:40 | 0
2023-12-16 13:41 | 0
2023-12-16 13:42 | 0
2023-12-16 13:43 | 0
2023-12-16 13:44 | 0
2023-12-16 13:45 | 0
2023-12-16 13:46 | 0
2023-12-16 13:47 | 0
2023-12-16 13:48 | 0
2023-12-16 13:49 | 0
2023-12-16 13:50 | 0
2023-12-16 13:51 | 0
2023-12-16 13:52 | 0
2023-12-16 13:53 | 0
2023-12-16 13:54 | 0
2023-12-16 13:55 | 0
2023-12-16 13:56 | 0
2023-12-16 13:57 | 0
2023-12-16 13:58 | 0
2023-12-16 13:59 | 0
2023-12-16 14:00 | 0
2023-12-16 14:01 | 0
2023-12-16 14:02 | 0
2023-12-16 14:03 | 0
2023-12-16 14:04 | 0
2023-12-16 14:05 | 0
2023-12-16 14:06 | 0
2023-12-16 14:07 | 0
2023-12-16 14:08 | 0
2023-12-16 14:09 | 0
2023-12-16 14:10 | 0
2023-12-16 14:11 | 0
2023-12-16 14:12 | 0
2023-12-16 14:13 | 0
2023-12-16 14:14 | 0
2023-12-16 14:15 | 0
2023-12-16 14:16 | 0
2023-12-16 14:17 | 0
2023-12-16 14:18 | 0
2023-12-16 14:19 | 0
2023-12-16 14:20 | 0
2023-12-16 14:21 | 0
2023-12-16 14:22 | 0
2023-12-16 14:23 | 0
2023-12-16 14:24 | 0
2023-12-16 14:25 | 0
2023-12-16 14:26 | 0
2023-12-16 14:27 | 0
2023-12-16 14:28 | 0
2023-12-16 14:29 | 0
2023-12-16 14:30 | 0
2023-12-16 14:31 | 0
2023-12-16 14:32 | 0
2023-12-16 14:33 | 0
2023-12-16 14:34 | 0
2023-12-16 14:35 | 0
2023-12-16 14:36 | 0
2023-12-16 14:37 | 0
2023-12-16 14:38 | 0
2023-12-16 14:39 | 0
2023-12-16 14:40 | 0.0752
2023-12-16 14:41 | 0.0859
2023-12-16 14:42 | 0.0857
2023-12-16 14:43 | 0.0858
2023-12-16 14:44 | 0.0861
2023-12-16 14:45 | 0.086
2023-12-16 14:46 | 0.0859
2023-12-16 14:47 | 0.0865
2023-12-16 14:48 | 0.0864
2023-12-16 14:49 | 0.0865
2023-12-16 14:50 | 0.0865
2023-12-16 14:51 | 0.0864
2023-12-16 14:52 | 0.0865
2023-12-16 14:53 | 0.0865
2023-12-16 14:54 | 0.0866
2023-12-16 14:55 | 0.0865
2023-12-16 14:56 | 0.0867
2023-12-16 14:57 | 0.0866
2023-12-16 14:58 | 0.0867
2023-12-16 14:59 | 0.0868
2023-12-16 15:00 | 0.0866
2023-12-16 15:01 | 0.0869
2023-12-16 15:02 | 0.0869
2023-12-16 15:03 | 0.0871
2023-12-16 15:04 | 0.0872
2023-12-16 15:05 | 0.087
2023-12-16 15:06 | 0.0869
2023-12-16 15:07 | 0.0867
2023-12-16 15:08 | 0.0867
2023-12-16 15:09 | 0.0866
2023-12-16 15:10 | 0.0867
2023-12-16 15:11 | 0.0867
2023-12-16 15:12 | 0.0871
2023-12-16 15:13 | 0.0868
2023-12-16 15:14 | 0.0868
2023-12-16 15:15 | 0.0866
2023-12-16 15:16 | 0.0864
2023-12-16 15:17 | 0.0866
2023-12-16 15:18 | 0.0864
2023-12-16 15:19 | 0.0867
2023-12-16 15:20 | 0.0869
2023-12-16 15:21 | 0.0869
2023-12-16 15:22 | 0.087
2023-12-16 15:23 | 0.0872
2023-12-16 15:24 | 0.087
2023-12-16 15:25 | 0.087
2023-12-16 15:26 | 0.087
2023-12-16 15:27 | 0.0869
2023-12-16 15:28 | 0.0869
2023-12-16 15:29 | 0.087
2023-12-16 15:30 | 0.0871
2023-12-16 15:31 | 0.0868
2023-12-16 15:32 | 0.087
2023-12-16 15:33 | 0.0869
2023-12-16 15:34 | 0.0869
2023-12-16 15:35 | 0.0868
2023-12-16 15:36 | 0.0867
2023-12-16 15:37 | 0.0869
2023-12-16 15:38 | 0.0869
2023-12-16 15:39 | 0.0867
2023-12-16 15:40 | 0.0871
2023-12-16 15:41 | 0.0871
2023-12-16 15:42 | 0.0872
2023-12-16 15:43 | 0.0873
2023-12-16 15:44 | 0.0872
2023-12-16 15:45 | 0.0874
2023-12-16 15:46 | 0.0873
2023-12-16 15:47 | 0.0874
2023-12-16 15:48 | 0.0875
2023-12-16 15:49 | 0.0878
2023-12-16 15:50 | 0.0876
2023-12-16 15:51 | 0.0875
2023-12-16 15:52 | 0.0876
2023-12-16 15:53 | 0.0877
2023-12-16 15:54 | 0.0876
2023-12-16 15:55 | 0.0874
2023-12-16 15:56 | 0.0872
2023-12-16 15:57 | 0.0875
2023-12-16 15:58 | 0.0876
2023-12-16 15:59 | 0.0873
2023-12-16 16:00 | 0.0874
2023-12-16 16:01 | 0.0874
2023-12-16 16:02 | 0.0876
2023-12-16 16:03 | 0.0875
2023-12-16 16:04 | 0.0872
2023-12-16 16:05 | 0.0873
2023-12-16 16:06 | 0.0876
2023-12-16 16:07 | 0.0877
2023-12-16 16:08 | 0.0877
2023-12-16 16:09 | 0.0875
2023-12-16 16:10 | 0.0876
2023-12-16 16:11 | 0.0877
2023-12-16 16:12 | 0.0876
2023-12-16 16:13 | 0.0878
2023-12-16 16:14 | 0.0875
2023-12-16 16:15 | 0.0878
2023-12-16 16:16 | 0.0878
2023-12-16 16:17 | 0.0876
2023-12-16 16:18 | 0.0875
2023-12-16 16:19 | 0.0874
2023-12-16 16:20 | 0.0873
2023-12-16 16:21 | 0.0875
2023-12-16 16:22 | 0.0876
2023-12-16 16:23 | 0.0877
2023-12-16 16:24 | 0.0876
2023-12-16 16:25 | 0.0874
2023-12-16 16:26 | 0.0875
2023-12-16 16:27 | 0.048
2023-12-16 16:28 | 0
2023-12-16 16:29 | 0
2023-12-16 16:30 | 0
2023-12-16 16:31 | 0
2023-12-16 16:32 | 0
2023-12-16 16:33 | 0
2023-12-16 16:34 | 0
2023-12-16 16:35 | 0
2023-12-16 16:36 | 0
2023-12-16 16:37 | 0
2023-12-16 16:38 | 0
2023-12-16 16:39 | 0
2023-12-16 16:40 | 0
2023-12-16 16:41 | 0
2023-12-16 16:42 | 0
2023-12-16 16:43 | 0
2023-12-16 16:44 | 0
2023-12-16 16:45 | 0.0218
2023-12-16 16:46 | 0.087
2023-12-16 16:47 | 0.0872
2023-12-16 16:48 | 0.0874
2023-12-16 16:49 | 0.0873
2023-12-16 16:50 | 0.0876
2023-12-16 16:51 | 0.0879
2023-12-16 16:52 | 0.0878
2023-12-16 16:53 | 0.0878
2023-12-16 16:54 | 0.0877
2023-12-16 16:55 | 0.0876
2023-12-16 16:56 | 0.0876
2023-12-16 16:57 | 0.0878
2023-12-16 16:58 | 0.0876
2023-12-16 16:59 | 0.0874
2023-12-16 17:00 | 0.0875
2023-12-16 17:01 | 0.0877
2023-12-16 17:02 | 0.0877
2023-12-16 17:03 | 0.088
2023-12-16 17:04 | 0.0879
2023-12-16 17:05 | 0.0878
2023-12-16 17:06 | 0.088
2023-12-16 17:07 | 0.0881
2023-12-16 17:08 | 0.0879
2023-12-16 17:09 | 0.0878
2023-12-16 17:10 | 0.0879
2023-12-16 17:11 | 0.0879
2023-12-16 17:12 | 0.0878
2023-12-16 17:13 | 0.0879
2023-12-16 17:14 | 0.0879
2023-12-16 17:15 | 0.0879
2023-12-16 17:16 | 0.0879
2023-12-16 17:17 | 0.0879
2023-12-16 17:18 | 0.0876
2023-12-16 17:19 | 0.0878
2023-12-16 17:20 | 0.0878
2023-12-16 17:21 | 0.0878
2023-12-16 17:22 | 0.0878
2023-12-16 17:23 | 0.0878
2023-12-16 17:24 | 0.0879
2023-12-16 17:25 | 0.0879
2023-12-16 17:26 | 0.0881
2023-12-16 17:27 | 0.0878
2023-12-16 17:28 | 0.0878
2023-12-16 17:29 | 0.0881
2023-12-16 17:30 | 0.0879
2023-12-16 17:31 | 0.0877
2023-12-16 17:32 | 0.0879
2023-12-16 17:33 | 0.0881
2023-12-16 17:34 | 0.0877
2023-12-16 17:35 | 0.0879
2023-12-16 17:36 | 0.088
2023-12-16 17:37 | 0.0878
2023-12-16 17:38 | 0.0878
2023-12-16 17:39 | 0.0876
2023-12-16 17:40 | 0.0455
2023-12-16 17:41 | 0
2023-12-16 17:42 | 0
2023-12-16 17:43 | 0
2023-12-16 17:44 | 0
2023-12-16 17:45 | 0
2023-12-16 17:46 | 0.0421
2023-12-16 17:47 | 0.0875
2023-12-16 17:48 | 0.0874
2023-12-16 17:49 | 0.0874
2023-12-16 17:50 | 0.0876
2023-12-16 17:51 | 0.0876
2023-12-16 17:52 | 0.0874
2023-12-16 17:53 | 0.0876
2023-12-16 17:54 | 0.0876
2023-12-16 17:55 | 0.0879
2023-12-16 17:56 | 0.0877
2023-12-16 17:57 | 0.0879
2023-12-16 17:58 | 0.0879
2023-12-16 17:59 | 0.0879
2023-12-16 18:00 | 0.0879
2023-12-16 18:01 | 0.088
2023-12-16 18:02 | 0.0881
2023-12-16 18:03 | 0.0879
2023-12-16 18:04 | 0.088
2023-12-16 18:05 | 0.0877
2023-12-16 18:06 | 0.0877
2023-12-16 18:07 | 0.0879
2023-12-16 18:08 | 0.0877
2023-12-16 18:09 | 0.0878
2023-12-16 18:10 | 0.0878
2023-12-16 18:11 | 0.0881
2023-12-16 18:12 | 0.088
2023-12-16 18:13 | 0.0878
2023-12-16 18:14 | 0.0878
2023-12-16 18:15 | 0.0879
2023-12-16 18:16 | 0.088
2023-12-16 18:17 | 0.0879
2023-12-16 18:18 | 0.0879
2023-12-16 18:19 | 0.088
2023-12-16 18:20 | 0.0881
2023-12-16 18:21 | 0.0881
2023-12-16 18:22 | 0.0881
2023-12-16 18:23 | 0.088
2023-12-16 18:24 | 0.0881
2023-12-16 18:25 | 0.088
2023-12-16 18:26 | 0.0882
2023-12-16 18:27 | 0.0881
2023-12-16 18:28 | 0.0879
2023-12-16 18:29 | 0.088
2023-12-16 18:30 | 0.0881
2023-12-16 18:31 | 0.0879
2023-12-16 18:32 | 0.0881
2023-12-16 18:33 | 0.0883
2023-12-16 18:34 | 0.0881
2023-12-16 18:35 | 0.0881
2023-12-16 18:36 | 0.0879
2023-12-16 18:37 | 0.0878
2023-12-16 18:38 | 0.0879
2023-12-16 18:39 | 0.0879
2023-12-16 18:40 | 0.0877
2023-12-16 18:41 | 0.0152
2023-12-16 18:42 | 0
2023-12-16 18:43 | 0
2023-12-16 18:44 | 0
2023-12-16 18:45 | 0
2023-12-16 18:46 | 0
2023-12-16 18:47 | 0.073
2023-12-16 18:48 | 0.0877
2023-12-16 18:49 | 0.0878
2023-12-16 18:50 | 0.088
2023-12-16 18:51 | 0.088
2023-12-16 18:52 | 0.0878
2023-12-16 18:53 | 0.0879
2023-12-16 18:54 | 0.0878
2023-12-16 18:55 | 0.0878
2023-12-16 18:56 | 0.0879
2023-12-16 18:57 | 0.088
2023-12-16 18:58 | 0.0878
2023-12-16 18:59 | 0.0878
2023-12-16 19:00 | 0.0879
2023-12-16 19:01 | 0.0878
2023-12-16 19:02 | 0.0875
2023-12-16 19:03 | 0.0876
2023-12-16 19:04 | 0.0878
2023-12-16 19:05 | 0.0876
2023-12-16 19:06 | 0.0876
2023-12-16 19:07 | 0.0877
2023-12-16 19:08 | 0.0876
2023-12-16 19:09 | 0.088
2023-12-16 19:10 | 0.0877
2023-12-16 19:11 | 0.0876
2023-12-16 19:12 | 0.0877
2023-12-16 19:13 | 0.0877
2023-12-16 19:14 | 0.088
2023-12-16 19:15 | 0.0881
2023-12-16 19:16 | 0.0879
2023-12-16 19:17 | 0.0879
2023-12-16 19:18 | 0.0879
2023-12-16 19:19 | 0.0879
2023-12-16 19:20 | 0.088
2023-12-16 19:21 | 0.0879
2023-12-16 19:22 | 0.0879
2023-12-16 19:23 | 0.0882
2023-12-16 19:24 | 0.0883
2023-12-16 19:25 | 0.0882
2023-12-16 19:26 | 0.0879
2023-12-16 19:27 | 0.0879
2023-12-16 19:28 | 0.0881
2023-12-16 19:29 | 0.0879
2023-12-16 19:30 | 0.0878
2023-12-16 19:31 | 0.0878
2023-12-16 19:32 | 0.0878
2023-12-16 19:33 | 0.0878
2023-12-16 19:34 | 0.0879
2023-12-16 19:35 | 0.088
2023-12-16 19:36 | 0.0879
2023-12-16 19:37 | 0.0883
2023-12-16 19:38 | 0.0882
2023-12-16 19:39 | 0.0882
2023-12-16 19:40 | 0.0879
2023-12-16 19:41 | 0.0677
2023-12-16 19:42 | 0
2023-12-16 19:43 | 0
2023-12-16 19:44 | 0
2023-12-16 19:45 | 0
2023-12-16 19:46 | 0
2023-12-16 19:47 | 0.0232
2023-12-16 19:48 | 0.0879
2023-12-16 19:49 | 0.0879
2023-12-16 19:50 | 0.088
2023-12-16 19:51 | 0.0879
2023-12-16 19:52 | 0.088
2023-12-16 19:53 | 0.0882
2023-12-16 19:54 | 0.0883
2023-12-16 19:55 | 0.0881
2023-12-16 19:56 | 0.088
2023-12-16 19:57 | 0.088
2023-12-16 19:58 | 0.0881
2023-12-16 19:59 | 0.0881
2023-12-16 20:00 | 0.0882
2023-12-16 20:01 | 0.0882
2023-12-16 20:02 | 0.088
2023-12-16 20:03 | 0.0881
2023-12-16 20:04 | 0.0881
2023-12-16 20:05 | 0.0879
2023-12-16 20:06 | 0.088
2023-12-16 20:07 | 0.0881
2023-12-16 20:08 | 0.0881
2023-12-16 20:09 | 0.088
2023-12-16 20:10 | 0.088
2023-12-16 20:11 | 0.0882
2023-12-16 20:12 | 0.0879
2023-12-16 20:13 | 0.0878
2023-12-16 20:14 | 0.0881
2023-12-16 20:15 | 0.0882
2023-12-16 20:16 | 0.0881
2023-12-16 20:17 | 0.0882
2023-12-16 20:18 | 0.0881
2023-12-16 20:19 | 0.0883
2023-12-16 20:20 | 0.0884
2023-12-16 20:21 | 0.0884
2023-12-16 20:22 | 0.0888
2023-12-16 20:23 | 0.089
2023-12-16 20:24 | 0.0889
2023-12-16 20:25 | 0.0888
2023-12-16 20:26 | 0.0887
2023-12-16 20:27 | 0.0886
2023-12-16 20:28 | 0.0887
2023-12-16 20:29 | 0.0885
2023-12-16 20:30 | 0.0887
2023-12-16 20:31 | 0.0889
2023-12-16 20:32 | 0.0888
2023-12-16 20:33 | 0.0889
2023-12-16 20:34 | 0.0889
2023-12-16 20:35 | 0.0886
2023-12-16 20:36 | 0.0884
2023-12-16 20:37 | 0.0882
2023-12-16 20:38 | 0.0882
2023-12-16 20:39 | 0.0883
2023-12-16 20:40 | 0.0882
2023-12-16 20:41 | 0.0882
2023-12-16 20:42 | 0.0883
2023-12-16 20:43 | 0.0882
2023-12-16 20:44 | 0.0883
2023-12-16 20:45 | 0.0883
2023-12-16 20:46 | 0.0884
2023-12-16 20:47 | 0.0886
2023-12-16 20:48 | 0.0888
2023-12-16 20:49 | 0.0886
2023-12-16 20:50 | 0.0883
2023-12-16 20:51 | 0.0883
2023-12-16 20:52 | 0.0885
2023-12-16 20:53 | 0.0885
2023-12-16 20:54 | 0.0888
2023-12-16 20:55 | 0.0885
2023-12-16 20:56 | 0.0886
2023-12-16 20:57 | 0.0887
2023-12-16 20:58 | 0.0886
2023-12-16 20:59 | 0.0886
2023-12-16 21:00 | 0.0887
2023-12-16 21:01 | 0.0886
2023-12-16 21:02 | 0.0882
2023-12-16 21:03 | 0.0881
2023-12-16 21:04 | 0.0883
2023-12-16 21:05 | 0.0882
2023-12-16 21:06 | 0.0881
2023-12-16 21:07 | 0.0881
2023-12-16 21:08 | 0.0881
2023-12-16 21:09 | 0.0881
2023-12-16 21:10 | 0.0882
2023-12-16 21:11 | 0.088
2023-12-16 21:12 | 0.0882
2023-12-16 21:13 | 0.088
2023-12-16 21:14 | 0.0879
2023-12-16 21:15 | 0.088
2023-12-16 21:16 | 0.0882
2023-12-16 21:17 | 0.0883
2023-12-16 21:18 | 0.0879
2023-12-16 21:19 | 0.0881
2023-12-16 21:20 | 0.088
2023-12-16 21:21 | 0.0883
2023-12-16 21:22 | 0.0883
2023-12-16 21:23 | 0.0881
2023-12-16 21:24 | 0.0883
2023-12-16 21:25 | 0.0882
2023-12-16 21:26 | 0.0882
2023-12-16 21:27 | 0.0882
2023-12-16 21:28 | 0.0884
2023-12-16 21:29 | 0.0884
2023-12-16 21:30 | 0.0884
2023-12-16 21:31 | 0.0885
2023-12-16 21:32 | 0.0884
2023-12-16 21:33 | 0.0887
2023-12-16 21:34 | 0.0883
2023-12-16 21:35 | 0.0883
2023-12-16 21:36 | 0.0885
2023-12-16 21:37 | 0.0884
2023-12-16 21:38 | 0.0882
2023-12-16 21:39 | 0.0883
2023-12-16 21:40 | 0.0884
2023-12-16 21:41 | 0.0883
2023-12-16 21:42 | 0.0741
2023-12-16 21:43 | 0
2023-12-16 21:44 | 0
2023-12-16 21:45 | 0
2023-12-16 21:46 | 0
2023-12-16 21:47 | 0
2023-12-16 21:48 | 0.0163
2023-12-16 21:49 | 0.0885
2023-12-16 21:50 | 0.0882
2023-12-16 21:51 | 0.0883
2023-12-16 21:52 | 0.0883
2023-12-16 21:53 | 0.0884
2023-12-16 21:54 | 0.0885
2023-12-16 21:55 | 0.0886
2023-12-16 21:56 | 0.0887
2023-12-16 21:57 | 0.0886
2023-12-16 21:58 | 0.0888
2023-12-16 21:59 | 0.0885
2023-12-16 22:00 | 0.0885
2023-12-16 22:01 | 0.0887
2023-12-16 22:02 | 0.0888
2023-12-16 22:03 | 0.0888
2023-12-16 22:04 | 0.0888
2023-12-16 22:05 | 0.0888
2023-12-16 22:06 | 0.0889
2023-12-16 22:07 | 0.0887
2023-12-16 22:08 | 0.0887
2023-12-16 22:09 | 0.0885
2023-12-16 22:10 | 0.0885
2023-12-16 22:11 | 0.0885
2023-12-16 22:12 | 0.0885
2023-12-16 22:13 | 0.0888
2023-12-16 22:14 | 0.0887
2023-12-16 22:15 | 0.0888
2023-12-16 22:16 | 0.0886
2023-12-16 22:17 | 0.0886
2023-12-16 22:18 | 0.0887
2023-12-16 22:19 | 0.0888
2023-12-16 22:20 | 0.0887
2023-12-16 22:21 | 0.0886
2023-12-16 22:22 | 0.0885
2023-12-16 22:23 | 0.0886
2023-12-16 22:24 | 0.0886
2023-12-16 22:25 | 0.0884
2023-12-16 22:26 | 0.0882
2023-12-16 22:27 | 0.0884
2023-12-16 22:28 | 0.0883
2023-12-16 22:29 | 0.0883
2023-12-16 22:30 | 0.0883
2023-12-16 22:31 | 0.0884
2023-12-16 22:32 | 0.0881
2023-12-16 22:33 | 0.0882
2023-12-16 22:34 | 0.0878
2023-12-16 22:35 | 0.0882
2023-12-16 22:36 | 0.0883
2023-12-16 22:37 | 0.0883
2023-12-16 22:38 | 0.0884
2023-12-16 22:39 | 0.0885
2023-12-16 22:40 | 0.0885
2023-12-16 22:41 | 0.0885
2023-12-16 22:42 | 0.0882
2023-12-16 22:43 | 0.0275
2023-12-16 22:44 | 0
2023-12-16 22:45 | 0
2023-12-16 22:46 | 0
2023-12-16 22:47 | 0
2023-12-16 22:48 | 0
2023-12-16 22:49 | 0.0641
2023-12-16 22:50 | 0.0883
2023-12-16 22:51 | 0.0884
2023-12-16 22:52 | 0.0881
2023-12-16 22:53 | 0.0882
2023-12-16 22:54 | 0.0883
2023-12-16 22:55 | 0.0883
2023-12-16 22:56 | 0.0884
2023-12-16 22:57 | 0.0885
2023-12-16 22:58 | 0.0884
2023-12-16 22:59 | 0.0884
2023-12-16 23:00 | 0.0887
2023-12-16 23:01 | 0.0888
2023-12-16 23:02 | 0.0888
2023-12-16 23:03 | 0.0888
2023-12-16 23:04 | 0.0887
2023-12-16 23:05 | 0.0887
2023-12-16 23:06 | 0.0888
2023-12-16 23:07 | 0.0889
2023-12-16 23:08 | 0.0887
2023-12-16 23:09 | 0.0888
2023-12-16 23:10 | 0.0884
2023-12-16 23:11 | 0.0886
2023-12-16 23:12 | 0.0884
2023-12-16 23:13 | 0.0885
2023-12-16 23:14 | 0.0886
2023-12-16 23:15 | 0.0885
2023-12-16 23:16 | 0.0887
2023-12-16 23:17 | 0.0886
2023-12-16 23:18 | 0.0884
2023-12-16 23:19 | 0.0884
2023-12-16 23:20 | 0.0885
2023-12-16 23:21 | 0.0885
2023-12-16 23:22 | 0.0886
2023-12-16 23:23 | 0.0886
2023-12-16 23:24 | 0.0884
2023-12-16 23:25 | 0.0885
2023-12-16 23:26 | 0.0884
2023-12-16 23:27 | 0.0885
2023-12-16 23:28 | 0.0886
2023-12-16 23:29 | 0.0885
2023-12-16 23:30 | 0.0885
2023-12-16 23:31 | 0.0887
2023-12-16 23:32 | 0.0886
2023-12-16 23:33 | 0.0884
2023-12-16 23:34 | 0.0886
2023-12-16 23:35 | 0.0886
2023-12-16 23:36 | 0.0886
2023-12-16 23:37 | 0.0887
2023-12-16 23:38 | 0.0888
2023-12-16 23:39 | 0.0888
2023-12-16 23:40 | 0.0883
2023-12-16 23:41 | 0.0887
2023-12-16 23:42 | 0.0885
2023-12-16 23:43 | 0.0644
2023-12-16 23:44 | 0
2023-12-16 23:45 | 0
2023-12-16 23:46 | 0
2023-12-16 23:47 | 0
2023-12-16 23:48 | 0
2023-12-16 23:49 | 0.0268
2023-12-16 23:50 | 0.0884
2023-12-16 23:51 | 0.0885
2023-12-16 23:52 | 0.0885
2023-12-16 23:53 | 0.0885
2023-12-16 23:54 | 0.0886
2023-12-16 23:55 | 0.0887
2023-12-16 23:56 | 0.0887
2023-12-16 23:57 | 0.0888
2023-12-16 23:58 | 0.0887
2023-12-16 23:59 | 0.0888
2023-12-17 | 0.0887
2023-12-17 00:01 | 0.0891
2023-12-17 00:02 | 0.0889
2023-12-17 00:03 | 0.0889
2023-12-17 00:04 | 0.0889
2023-12-17 00:05 | 0.0888
2023-12-17 00:06 | 0.0889
2023-12-17 00:07 | 0.0889
2023-12-17 00:08 | 0.0889
2023-12-17 00:09 | 0.089
2023-12-17 00:10 | 0.0892
2023-12-17 00:11 | 0.0888
2023-12-17 00:12 | 0.0889
2023-12-17 00:13 | 0.0889
2023-12-17 00:14 | 0.0888
2023-12-17 00:15 | 0.0887
2023-12-17 00:16 | 0.0889
2023-12-17 00:17 | 0.089
2023-12-17 00:18 | 0.0889
2023-12-17 00:19 | 0.0889
2023-12-17 00:20 | 0.0889
2023-12-17 00:21 | 0.089
2023-12-17 00:22 | 0.089
2023-12-17 00:23 | 0.089
2023-12-17 00:24 | 0.089
2023-12-17 00:25 | 0.089
2023-12-17 00:26 | 0.0891
2023-12-17 00:27 | 0.0889
2023-12-17 00:28 | 0.0891
2023-12-17 00:29 | 0.089
2023-12-17 00:30 | 0.089
2023-12-17 00:31 | 0.0886
2023-12-17 00:32 | 0.0885
2023-12-17 00:33 | 0.0885
2023-12-17 00:34 | 0.0884
2023-12-17 00:35 | 0.0886
2023-12-17 00:36 | 0.0884
2023-12-17 00:37 | 0.0885
2023-12-17 00:38 | 0.0885
2023-12-17 00:39 | 0.0884
2023-12-17 00:40 | 0.0883
2023-12-17 00:41 | 0.0884
2023-12-17 00:42 | 0.0884
2023-12-17 00:43 | 0.0882
2023-12-17 00:44 | 0.0099
2023-12-17 00:45 | 0
2023-12-17 00:46 | 0
2023-12-17 00:47 | 0
2023-12-17 00:48 | 0
2023-12-17 00:49 | 0
2023-12-17 00:50 | 0.0814
2023-12-17 00:51 | 0.0883
2023-12-17 00:52 | 0.0883
2023-12-17 00:53 | 0.0885
2023-12-17 00:54 | 0.0886
2023-12-17 00:55 | 0.0883
2023-12-17 00:56 | 0.0882
2023-12-17 00:57 | 0.0882
2023-12-17 00:58 | 0.0882
2023-12-17 00:59 | 0.0881
2023-12-17 01:00 | 0.0883
2023-12-17 01:01 | 0.0884
2023-12-17 01:02 | 0.0884
2023-12-17 01:03 | 0.0886
2023-12-17 01:04 | 0.0883
2023-12-17 01:05 | 0.0883
2023-12-17 01:06 | 0.0884
2023-12-17 01:07 | 0.0883
2023-12-17 01:08 | 0.0884
2023-12-17 01:09 | 0.0883
2023-12-17 01:10 | 0.0882
2023-12-17 01:11 | 0.0884
2023-12-17 01:12 | 0.0888
2023-12-17 01:13 | 0.0885
2023-12-17 01:14 | 0.0886
2023-12-17 01:15 | 0.0883
2023-12-17 01:16 | 0.0886
2023-12-17 01:17 | 0.0884
2023-12-17 01:18 | 0.0885
2023-12-17 01:19 | 0.0885
2023-12-17 01:20 | 0.0886
2023-12-17 01:21 | 0.0889
2023-12-17 01:22 | 0.0884
2023-12-17 01:23 | 0.0886
2023-12-17 01:24 | 0.0885
2023-12-17 01:25 | 0.0885
2023-12-17 01:26 | 0.0885
2023-12-17 01:27 | 0.0885
2023-12-17 01:28 | 0.0886
2023-12-17 01:29 | 0.0886
2023-12-17 01:30 | 0.0885
2023-12-17 01:31 | 0.0885
2023-12-17 01:32 | 0.0884
2023-12-17 01:33 | 0.0885
2023-12-17 01:34 | 0.0887
2023-12-17 01:35 | 0.0887
2023-12-17 01:36 | 0.0887
2023-12-17 01:37 | 0.0885
2023-12-17 01:38 | 0.0882
2023-12-17 01:39 | 0.0885
2023-12-17 01:40 | 0.0885
2023-12-17 01:41 | 0.0884
2023-12-17 01:42 | 0.0883
2023-12-17 01:43 | 0.0885
2023-12-17 01:44 | 0.0415
2023-12-17 01:45 | 0
2023-12-17 01:46 | 0
2023-12-17 01:47 | 0
2023-12-17 01:48 | 0
2023-12-17 01:49 | 0
2023-12-17 01:50 | 0.0508
2023-12-17 01:51 | 0.0881
2023-12-17 01:52 | 0.0882
2023-12-17 01:53 | 0.0882
2023-12-17 01:54 | 0.0882
2023-12-17 01:55 | 0.0883
2023-12-17 01:56 | 0.0882
2023-12-17 01:57 | 0.0886
2023-12-17 01:58 | 0.0888
2023-12-17 01:59 | 0.0883
2023-12-17 02:00 | 0.0886
2023-12-17 02:01 | 0.0886
2023-12-17 02:02 | 0.0885
2023-12-17 02:03 | 0.0884
2023-12-17 02:04 | 0.0884
2023-12-17 02:05 | 0.0884
2023-12-17 02:06 | 0.0883
2023-12-17 02:07 | 0.0883
2023-12-17 02:08 | 0.0885
2023-12-17 02:09 | 0.0886
2023-12-17 02:10 | 0.0885
2023-12-17 02:11 | 0.0887
2023-12-17 02:12 | 0.0888
2023-12-17 02:13 | 0.0885
2023-12-17 02:14 | 0.0886
2023-12-17 02:15 | 0.0888
2023-12-17 02:16 | 0.0884
2023-12-17 02:17 | 0.0885
2023-12-17 02:18 | 0.0886
2023-12-17 02:19 | 0.0885
2023-12-17 02:20 | 0.0885
2023-12-17 02:21 | 0.0884
2023-12-17 02:22 | 0.0885
2023-12-17 02:23 | 0.0887
2023-12-17 02:24 | 0.089
2023-12-17 02:25 | 0.0888
2023-12-17 02:26 | 0.0888
2023-12-17 02:27 | 0.0888
2023-12-17 02:28 | 0.0887
2023-12-17 02:29 | 0.0889
2023-12-17 02:30 | 0.0887
2023-12-17 02:31 | 0.0887
2023-12-17 02:32 | 0.0888
2023-12-17 02:33 | 0.0887
2023-12-17 02:34 | 0.0886
2023-12-17 02:35 | 0.0886
2023-12-17 02:36 | 0.0886
2023-12-17 02:37 | 0.0886
2023-12-17 02:38 | 0.0888
2023-12-17 02:39 | 0.0888
2023-12-17 02:40 | 0.0889
2023-12-17 02:41 | 0.0887
2023-12-17 02:42 | 0.0887
2023-12-17 02:43 | 0.0886
2023-12-17 02:44 | 0.0698
2023-12-17 02:45 | 0
2023-12-17 02:46 | 0
2023-12-17 02:47 | 0
2023-12-17 02:48 | 0
2023-12-17 02:49 | 0
2023-12-17 02:50 | 0.0225
2023-12-17 02:51 | 0.0884
2023-12-17 02:52 | 0.0886
2023-12-17 02:53 | 0.0885
2023-12-17 02:54 | 0.0884
2023-12-17 02:55 | 0.0884
2023-12-17 02:56 | 0.0883
2023-12-17 02:57 | 0.0884
2023-12-17 02:58 | 0.0882
2023-12-17 02:59 | 0.0884
2023-12-17 03:00 | 0.0883
2023-12-17 03:01 | 0.0883
2023-12-17 03:02 | 0.0885
2023-12-17 03:03 | 0.0881
2023-12-17 03:04 | 0.0883
2023-12-17 03:05 | 0.0881
2023-12-17 03:06 | 0.0883
2023-12-17 03:07 | 0.0883
2023-12-17 03:08 | 0.0882
2023-12-17 03:09 | 0.0881
2023-12-17 03:10 | 0.0882
2023-12-17 03:11 | 0.0881
2023-12-17 03:12 | 0.0883
2023-12-17 03:13 | 0.0884
2023-12-17 03:14 | 0.0884
2023-12-17 03:15 | 0.0884
2023-12-17 03:16 | 0.0883
2023-12-17 03:17 | 0.0885
2023-12-17 03:18 | 0.0887
2023-12-17 03:19 | 0.0883
2023-12-17 03:20 | 0.0884
2023-12-17 03:21 | 0.0883
2023-12-17 03:22 | 0.0884
2023-12-17 03:23 | 0.0882
2023-12-17 03:24 | 0.0883
2023-12-17 03:25 | 0.0884
2023-12-17 03:26 | 0.0884
2023-12-17 03:27 | 0.0885
2023-12-17 03:28 | 0.0883
2023-12-17 03:29 | 0.0883
2023-12-17 03:30 | 0.0884
2023-12-17 03:31 | 0.0883
2023-12-17 03:32 | 0.0885
2023-12-17 03:33 | 0.0885
2023-12-17 03:34 | 0.0884
2023-12-17 03:35 | 0.0885
2023-12-17 03:36 | 0.0886
2023-12-17 03:37 | 0.0882
2023-12-17 03:38 | 0.0882
2023-12-17 03:39 | 0.0882
2023-12-17 03:40 | 0.0882
2023-12-17 03:41 | 0.0882
2023-12-17 03:42 | 0.0883
2023-12-17 03:43 | 0.0884
2023-12-17 03:44 | 0.0883
2023-12-17 03:45 | 0.007
2023-12-17 03:46 | 0
2023-12-17 03:47 | 0
2023-12-17 03:48 | 0
2023-12-17 03:49 | 0
2023-12-17 03:50 | 0
2023-12-17 03:51 | 0.0852
2023-12-17 03:52 | 0.088
2023-12-17 03:53 | 0.0882
2023-12-17 03:54 | 0.088
2023-12-17 03:55 | 0.0878
2023-12-17 03:56 | 0.088
2023-12-17 03:57 | 0.0882
2023-12-17 03:58 | 0.0879
2023-12-17 03:59 | 0.0881
2023-12-17 04:00 | 0.0881
2023-12-17 04:01 | 0.088
2023-12-17 04:02 | 0.0882
2023-12-17 04:03 | 0.0881
2023-12-17 04:04 | 0.088
2023-12-17 04:05 | 0.088
2023-12-17 04:06 | 0.0878
2023-12-17 04:07 | 0.088
2023-12-17 04:08 | 0.088
2023-12-17 04:09 | 0.0882
2023-12-17 04:10 | 0.0882
2023-12-17 04:11 | 0.0881
2023-12-17 04:12 | 0.0882
2023-12-17 04:13 | 0.0883
2023-12-17 04:14 | 0.088
2023-12-17 04:15 | 0.088
2023-12-17 04:16 | 0.0881
2023-12-17 04:17 | 0.088
2023-12-17 04:18 | 0.0881
2023-12-17 04:19 | 0.0881
2023-12-17 04:20 | 0.088
2023-12-17 04:21 | 0.0881
2023-12-17 04:22 | 0.0881
2023-12-17 04:23 | 0.0882
2023-12-17 04:24 | 0.088
2023-12-17 04:25 | 0.0881
2023-12-17 04:26 | 0.0882
2023-12-17 04:27 | 0.0883
2023-12-17 04:28 | 0.0883
2023-12-17 04:29 | 0.0883
2023-12-17 04:30 | 0.0881
2023-12-17 04:31 | 0.088
2023-12-17 04:32 | 0.0883
2023-12-17 04:33 | 0.0882
2023-12-17 04:34 | 0.0883
2023-12-17 04:35 | 0.0883
2023-12-17 04:36 | 0.0881
2023-12-17 04:37 | 0.0881
2023-12-17 04:38 | 0.0883
2023-12-17 04:39 | 0.0881
2023-12-17 04:40 | 0.0882
2023-12-17 04:41 | 0.0882
2023-12-17 04:42 | 0.0881
2023-12-17 04:43 | 0.0881
2023-12-17 04:44 | 0.0881
2023-12-17 04:45 | 0.0295
2023-12-17 04:46 | 0
2023-12-17 04:47 | 0
2023-12-17 04:48 | 0
2023-12-17 04:49 | 0
2023-12-17 04:50 | 0
2023-12-17 04:51 | 0.0628
2023-12-17 04:52 | 0.0879
2023-12-17 04:53 | 0.0882
2023-12-17 04:54 | 0.0883
2023-12-17 04:55 | 0.0881
2023-12-17 04:56 | 0.088
2023-12-17 04:57 | 0.0879
2023-12-17 04:58 | 0.0879
2023-12-17 04:59 | 0.0877
2023-12-17 05:00 | 0.0877
2023-12-17 05:01 | 0.0876
2023-12-17 05:02 | 0.0876
2023-12-17 05:03 | 0.088
2023-12-17 05:04 | 0.0882
2023-12-17 05:05 | 0.0884
2023-12-17 05:06 | 0.0886
2023-12-17 05:07 | 0.0886
2023-12-17 05:08 | 0.0886
2023-12-17 05:09 | 0.0886
2023-12-17 05:10 | 0.0885
2023-12-17 05:11 | 0.0885
2023-12-17 05:12 | 0.0883
2023-12-17 05:13 | 0.0887
2023-12-17 05:14 | 0.0887
2023-12-17 05:15 | 0.0889
2023-12-17 05:16 | 0.0888
2023-12-17 05:17 | 0.0889
2023-12-17 05:18 | 0.0886
2023-12-17 05:19 | 0.0887
2023-12-17 05:20 | 0.0878
2023-12-17 05:21 | 0.0877
2023-12-17 05:22 | 0.0875
2023-12-17 05:23 | 0.0879
2023-12-17 05:24 | 0.0877
2023-12-17 05:25 | 0.0867
2023-12-17 05:26 | 0.0864
2023-12-17 05:27 | 0.0876
2023-12-17 05:28 | 0.0882
2023-12-17 05:29 | 0.0879
2023-12-17 05:30 | 0.0863
2023-12-17 05:31 | 0.0862
2023-12-17 05:32 | 0.0865
2023-12-17 05:33 | 0.087
2023-12-17 05:34 | 0.087
2023-12-17 05:35 | 0.0868
2023-12-17 05:36 | 0.087
2023-12-17 05:37 | 0.0867
2023-12-17 05:38 | 0.0868
2023-12-17 05:39 | 0.0869
2023-12-17 05:40 | 0.0869
2023-12-17 05:41 | 0.087
2023-12-17 05:42 | 0.087
2023-12-17 05:43 | 0.0872
2023-12-17 05:44 | 0.0874
2023-12-17 05:45 | 0.0481
2023-12-17 05:46 | 0
2023-12-17 05:47 | 0
2023-12-17 05:48 | 0
2023-12-17 05:49 | 0
2023-12-17 05:50 | 0
2023-12-17 05:51 | 0.0446
2023-12-17 05:52 | 0.0885
2023-12-17 05:53 | 0.0872
2023-12-17 05:54 | 0.0871
2023-12-17 05:55 | 0.0872
2023-12-17 05:56 | 0.0872
2023-12-17 05:57 | 0.0872
2023-12-17 05:58 | 0.0875
2023-12-17 05:59 | 0.087
2023-12-17 06:00 | 0.0869
2023-12-17 06:01 | 0.087
2023-12-17 06:02 | 0.0868
2023-12-17 06:03 | 0.0871
2023-12-17 06:04 | 0.0869
2023-12-17 06:05 | 0.0873
2023-12-17 06:06 | 0.0869
2023-12-17 06:07 | 0.0868
2023-12-17 06:08 | 0.0867
2023-12-17 06:09 | 0.0865
2023-12-17 06:10 | 0.0868
2023-12-17 06:11 | 0.0867
2023-12-17 06:12 | 0.0869
2023-12-17 06:13 | 0.0867
2023-12-17 06:14 | 0.0867
2023-12-17 06:15 | 0.0868
2023-12-17 06:16 | 0.0877
2023-12-17 06:17 | 0.0881
2023-12-17 06:18 | 0.088
2023-12-17 06:19 | 0.0882
2023-12-17 06:20 | 0.0884
2023-12-17 06:21 | 0.088
2023-12-17 06:22 | 0.0882
2023-12-17 06:23 | 0.0882
2023-12-17 06:24 | 0.0883
2023-12-17 06:25 | 0.0882
2023-12-17 06:26 | 0.088
2023-12-17 06:27 | 0.0884
2023-12-17 06:28 | 0.0881
2023-12-17 06:29 | 0.0883
2023-12-17 06:30 | 0.0882
2023-12-17 06:31 | 0.088
2023-12-17 06:32 | 0.0882
2023-12-17 06:33 | 0.0879
2023-12-17 06:34 | 0.0881
2023-12-17 06:35 | 0.0879
2023-12-17 06:36 | 0.0881
2023-12-17 06:37 | 0.0882
2023-12-17 06:38 | 0.0878
2023-12-17 06:39 | 0.0882
2023-12-17 06:40 | 0.0879
2023-12-17 06:41 | 0.0881
2023-12-17 06:42 | 0.0884
2023-12-17 06:43 | 0.0882
2023-12-17 06:44 | 0.0881
2023-12-17 06:45 | 0.0673
2023-12-17 06:46 | 0
2023-12-17 06:47 | 0
2023-12-17 06:48 | 0
2023-12-17 06:49 | 0
2023-12-17 06:50 | 0
2023-12-17 06:51 | 0.0247
2023-12-17 06:52 | 0.0881
2023-12-17 06:53 | 0.0876
2023-12-17 06:54 | 0.088
2023-12-17 06:55 | 0.0877
2023-12-17 06:56 | 0.0877
2023-12-17 06:57 | 0.0878
2023-12-17 06:58 | 0.088
2023-12-17 06:59 | 0.088
2023-12-17 07:00 | 0.0881
2023-12-17 07:01 | 0.0877
2023-12-17 07:02 | 0.0877
2023-12-17 07:03 | 0.0879
2023-12-17 07:04 | 0.0879
2023-12-17 07:05 | 0.0878
2023-12-17 07:06 | 0.0878
2023-12-17 07:07 | 0.0879
2023-12-17 07:08 | 0.088
2023-12-17 07:09 | 0.0877
2023-12-17 07:10 | 0.0881
2023-12-17 07:11 | 0.0884
2023-12-17 07:12 | 0.0883
2023-12-17 07:13 | 0.0881
2023-12-17 07:14 | 0.0878
2023-12-17 07:15 | 0.0879
2023-12-17 07:16 | 0.0876
2023-12-17 07:17 | 0.0876
2023-12-17 07:18 | 0.0875
2023-12-17 07:19 | 0.0874
2023-12-17 07:20 | 0.0875
2023-12-17 07:21 | 0.0876
2023-12-17 07:22 | 0.0877
2023-12-17 07:23 | 0.0879
2023-12-17 07:24 | 0.0879
2023-12-17 07:25 | 0.0881
2023-12-17 07:26 | 0.0878
2023-12-17 07:27 | 0.088
2023-12-17 07:28 | 0.0876
2023-12-17 07:29 | 0.0878
2023-12-17 07:30 | 0.0876
2023-12-17 07:31 | 0.0875
2023-12-17 07:32 | 0.0878
2023-12-17 07:33 | 0.0876
2023-12-17 07:34 | 0.0875
2023-12-17 07:35 | 0.0874
2023-12-17 07:36 | 0.0873
2023-12-17 07:37 | 0.0873
2023-12-17 07:38 | 0.0874
2023-12-17 07:39 | 0.0874
2023-12-17 07:40 | 0.0874
2023-12-17 07:41 | 0.0874
2023-12-17 07:42 | 0.0874
2023-12-17 07:43 | 0.0872
2023-12-17 07:44 | 0.0873
2023-12-17 07:45 | 0.0869
2023-12-17 07:46 | 0.0038
2023-12-17 07:47 | 0
2023-12-17 07:48 | 0
2023-12-17 07:49 | 0
2023-12-17 07:50 | 0
2023-12-17 07:51 | 0
2023-12-17 07:52 | 0.0879
2023-12-17 07:53 | 0.0875
2023-12-17 07:54 | 0.0877
2023-12-17 07:55 | 0.0874
2023-12-17 07:56 | 0.0875
2023-12-17 07:57 | 0.0874
2023-12-17 07:58 | 0.0876
2023-12-17 07:59 | 0.0877
2023-12-17 08:00 | 0.0871
2023-12-17 08:01 | 0.0875
2023-12-17 08:02 | 0.0874
2023-12-17 08:03 | 0.0876
2023-12-17 08:04 | 0.0875
2023-12-17 08:05 | 0.0872
2023-12-17 08:06 | 0.0874
2023-12-17 08:07 | 0.0874
2023-12-17 08:08 | 0.088
2023-12-17 08:09 | 0.088
2023-12-17 08:10 | 0.0879
2023-12-17 08:11 | 0.0881
2023-12-17 08:12 | 0.0878
2023-12-17 08:13 | 0.088
2023-12-17 08:14 | 0.0877
2023-12-17 08:15 | 0.0881
2023-12-17 08:16 | 0.0881
2023-12-17 08:17 | 0.0879
2023-12-17 08:18 | 0.088
2023-12-17 08:19 | 0.0881
2023-12-17 08:20 | 0.0881
2023-12-17 08:21 | 0.0879
2023-12-17 08:22 | 0.0878
2023-12-17 08:23 | 0.088
2023-12-17 08:24 | 0.0878
2023-12-17 08:25 | 0.0881
2023-12-17 08:26 | 0.0878
2023-12-17 08:27 | 0.0878
2023-12-17 08:28 | 0.088
2023-12-17 08:29 | 0.0877
2023-12-17 08:30 | 0.0878
2023-12-17 08:31 | 0.088
2023-12-17 08:32 | 0.0878
2023-12-17 08:33 | 0.0879
2023-12-17 08:34 | 0.0881
2023-12-17 08:35 | 0.088
2023-12-17 08:36 | 0.0878
2023-12-17 08:37 | 0.088
2023-12-17 08:38 | 0.0875
2023-12-17 08:39 | 0.0866
2023-12-17 08:40 | 0.0865
2023-12-17 08:41 | 0.0866
2023-12-17 08:42 | 0.0873
2023-12-17 08:43 | 0.0878
2023-12-17 08:44 | 0.0868
2023-12-17 08:45 | 0.0866
2023-12-17 08:46 | 0.0298
2023-12-17 08:47 | 0
2023-12-17 08:48 | 0
2023-12-17 08:49 | 0
2023-12-17 08:50 | 0
2023-12-17 08:51 | 0
2023-12-17 08:52 | 0.0614
2023-12-17 08:53 | 0.0873
2023-12-17 08:54 | 0.0877
2023-12-17 08:55 | 0.0877
2023-12-17 08:56 | 0.0877
2023-12-17 08:57 | 0.0878
2023-12-17 08:58 | 0.088
2023-12-17 08:59 | 0.0877
2023-12-17 09:00 | 0.0876
2023-12-17 09:01 | 0.0876
2023-12-17 09:02 | 0.0876
2023-12-17 09:03 | 0.0877
2023-12-17 09:04 | 0.0874
2023-12-17 09:05 | 0.0875
2023-12-17 09:06 | 0.0872
2023-12-17 09:07 | 0.0875
2023-12-17 09:08 | 0.0875
2023-12-17 09:09 | 0.0875
2023-12-17 09:10 | 0.0875
2023-12-17 09:11 | 0.0875
2023-12-17 09:12 | 0.0873
2023-12-17 09:13 | 0.0875
2023-12-17 09:14 | 0.0875
2023-12-17 09:15 | 0.0874
2023-12-17 09:16 | 0.0876
2023-12-17 09:17 | 0.0873
2023-12-17 09:18 | 0.0873
2023-12-17 09:19 | 0.0875
2023-12-17 09:20 | 0.0874
2023-12-17 09:21 | 0.0875
2023-12-17 09:22 | 0.0873
2023-12-17 09:23 | 0.0875
2023-12-17 09:24 | 0.0875
2023-12-17 09:25 | 0.0875
2023-12-17 09:26 | 0.0872
2023-12-17 09:27 | 0.0872
2023-12-17 09:28 | 0.0872
2023-12-17 09:29 | 0.0874
2023-12-17 09:30 | 0.0875
2023-12-17 09:31 | 0.0875
2023-12-17 09:32 | 0.0871
2023-12-17 09:33 | 0.0869
2023-12-17 09:34 | 0.0873
2023-12-17 09:35 | 0.0873
2023-12-17 09:36 | 0.0873
2023-12-17 09:37 | 0.0872
2023-12-17 09:38 | 0.0871
2023-12-17 09:39 | 0.0872
2023-12-17 09:40 | 0.0869
2023-12-17 09:41 | 0.0871
2023-12-17 09:42 | 0.0871
2023-12-17 09:43 | 0.0871
2023-12-17 09:44 | 0.0873
2023-12-17 09:45 | 0.0873
2023-12-17 09:46 | 0.0548
2023-12-17 09:47 | 0
2023-12-17 09:48 | 0
2023-12-17 09:49 | 0
2023-12-17 09:50 | 0
2023-12-17 09:51 | 0
2023-12-17 09:52 | 0.0364
2023-12-17 09:53 | 0.087
2023-12-17 09:54 | 0.0871
2023-12-17 09:55 | 0.087
2023-12-17 09:56 | 0.0872
2023-12-17 09:57 | 0.0869
2023-12-17 09:58 | 0.0866
2023-12-17 09:59 | 0.087
2023-12-17 10:00 | 0.0872
2023-12-17 10:01 | 0.087
2023-12-17 10:02 | 0.0873
2023-12-17 10:03 | 0.0874
2023-12-17 10:04 | 0.0873
2023-12-17 10:05 | 0.0873
2023-12-17 10:06 | 0.0874
2023-12-17 10:07 | 0.0876
2023-12-17 10:08 | 0.0874
2023-12-17 10:09 | 0.0874
2023-12-17 10:10 | 0.0874
2023-12-17 10:11 | 0.0875
2023-12-17 10:12 | 0.0873
2023-12-17 10:13 | 0.0873
2023-12-17 10:14 | 0.0875
2023-12-17 10:15 | 0.0876
2023-12-17 10:16 | 0.0874
2023-12-17 10:17 | 0.0873
2023-12-17 10:18 | 0.0877
2023-12-17 10:19 | 0.0876
2023-12-17 10:20 | 0.0872
2023-12-17 10:21 | 0.0874
2023-12-17 10:22 | 0.0875
2023-12-17 10:23 | 0.0876
2023-12-17 10:24 | 0.0872
2023-12-17 10:25 | 0.0874
2023-12-17 10:26 | 0.0875
2023-12-17 10:27 | 0.0876
2023-12-17 10:28 | 0.0873
2023-12-17 10:29 | 0.0875
2023-12-17 10:30 | 0.0875
2023-12-17 10:31 | 0.0873
2023-12-17 10:32 | 0.0874
2023-12-17 10:33 | 0.0877
2023-12-17 10:34 | 0.0877
2023-12-17 10:35 | 0.0877
2023-12-17 10:36 | 0.0875
2023-12-17 10:37 | 0.0872
2023-12-17 10:38 | 0.087
2023-12-17 10:39 | 0.087
2023-12-17 10:40 | 0.0869
2023-12-17 10:41 | 0.087
2023-12-17 10:42 | 0.087
2023-12-17 10:43 | 0.0867
2023-12-17 10:44 | 0.0867
2023-12-17 10:45 | 0.0868
2023-12-17 10:46 | 0.0771
2023-12-17 10:47 | 0
2023-12-17 10:48 | 0
2023-12-17 10:49 | 0
2023-12-17 10:50 | 0
2023-12-17 10:51 | 0
2023-12-17 10:52 | 0.0135
2023-12-17 10:53 | 0.0863
2023-12-17 10:54 | 0.0865
2023-12-17 10:55 | 0.0866
2023-12-17 10:56 | 0.0865
2023-12-17 10:57 | 0.0864
2023-12-17 10:58 | 0.0866
2023-12-17 10:59 | 0.0866
2023-12-17 11:00 | 0.0867
2023-12-17 11:01 | 0.0865
2023-12-17 11:02 | 0.0864
2023-12-17 11:03 | 0.0867
2023-12-17 11:04 | 0.0865
2023-12-17 11:05 | 0.0867
2023-12-17 11:06 | 0.0863
2023-12-17 11:07 | 0.0865
2023-12-17 11:08 | 0.0867
2023-12-17 11:09 | 0.0865
2023-12-17 11:10 | 0.0865
2023-12-17 11:11 | 0.0866
2023-12-17 11:12 | 0.0866
2023-12-17 11:13 | 0.0865
2023-12-17 11:14 | 0.0867
2023-12-17 11:15 | 0.0869
2023-12-17 11:16 | 0.0869
2023-12-17 11:17 | 0.087
2023-12-17 11:18 | 0.087
2023-12-17 11:19 | 0.0871
2023-12-17 11:20 | 0.0869
2023-12-17 11:21 | 0.0872
2023-12-17 11:22 | 0.0872
2023-12-17 11:23 | 0.0867
2023-12-17 11:24 | 0.087
2023-12-17 11:25 | 0.0868
2023-12-17 11:26 | 0.0867
2023-12-17 11:27 | 0.0868
2023-12-17 11:28 | 0.0867
2023-12-17 11:29 | 0.0866
2023-12-17 11:30 | 0.0869
2023-12-17 11:31 | 0.0866
2023-12-17 11:32 | 0.0866
2023-12-17 11:33 | 0.0867
2023-12-17 11:34 | 0.0869
2023-12-17 11:35 | 0.0868
2023-12-17 11:36 | 0.0868
2023-12-17 11:37 | 0.0865
2023-12-17 11:38 | 0.0864
2023-12-17 11:39 | 0.0868
2023-12-17 11:40 | 0.0863
2023-12-17 11:41 | 0.0864
2023-12-17 11:42 | 0.0866
2023-12-17 11:43 | 0.0866
2023-12-17 11:44 | 0.0863
2023-12-17 11:45 | 0.0866
2023-12-17 11:46 | 0.0867
2023-12-17 11:47 | 0.0137
2023-12-17 11:48 | 0
2023-12-17 11:49 | 0
2023-12-17 11:50 | 0
2023-12-17 11:51 | 0
2023-12-17 11:52 | 0
2023-12-17 11:53 | 0.0771
2023-12-17 11:54 | 0.086
2023-12-17 11:55 | 0.086
2023-12-17 11:56 | 0.086
2023-12-17 11:57 | 0.086
2023-12-17 11:58 | 0.0859
2023-12-17 11:59 | 0.0858
2023-12-17 12:00 | 0.086
2023-12-17 12:01 | 0.0861
2023-12-17 12:02 | 0.0865
2023-12-17 12:03 | 0.0862
2023-12-17 12:04 | 0.0863
2023-12-17 12:05 | 0.0864
2023-12-17 12:06 | 0.0863
2023-12-17 12:07 | 0.0862
2023-12-17 12:08 | 0.0861
2023-12-17 12:09 | 0.0862
2023-12-17 12:10 | 0.0861
2023-12-17 12:11 | 0.0861
2023-12-17 12:12 | 0.0859
2023-12-17 12:13 | 0.0861
2023-12-17 12:14 | 0.0859
2023-12-17 12:15 | 0.086
2023-12-17 12:16 | 0.086
2023-12-17 12:17 | 0.086
2023-12-17 12:18 | 0.086
2023-12-17 12:19 | 0.0858
2023-12-17 12:20 | 0.086
2023-12-17 12:21 | 0.086
2023-12-17 12:22 | 0.086
2023-12-17 12:23 | 0.086
2023-12-17 12:24 | 0.0861
2023-12-17 12:25 | 0.0859
2023-12-17 12:26 | 0.0862
2023-12-17 12:27 | 0.086
2023-12-17 12:28 | 0.0863
2023-12-17 12:29 | 0.0861
2023-12-17 12:30 | 0.0861
2023-12-17 12:31 | 0.0862
2023-12-17 12:32 | 0.0862
2023-12-17 12:33 | 0.0865
2023-12-17 12:34 | 0.0861
2023-12-17 12:35 | 0.0861
2023-12-17 12:36 | 0.0861
2023-12-17 12:37 | 0.086
2023-12-17 12:38 | 0.0862
2023-12-17 12:39 | 0.0862
2023-12-17 12:40 | 0.0862
2023-12-17 12:41 | 0.0859
2023-12-17 12:42 | 0.0863
2023-12-17 12:43 | 0.0862
2023-12-17 12:44 | 0.0861
2023-12-17 12:45 | 0.0862
2023-12-17 12:46 | 0.0861
2023-12-17 12:47 | 0.0362
2023-12-17 12:48 | 0
2023-12-17 12:49 | 0
2023-12-17 12:50 | 0
2023-12-17 12:51 | 0
2023-12-17 12:52 | 0
2023-12-17 12:53 | 0.0536
2023-12-17 12:54 | 0.0857
2023-12-17 12:55 | 0.0856
2023-12-17 12:56 | 0.0858
2023-12-17 12:57 | 0.0859
2023-12-17 12:58 | 0.0863
2023-12-17 12:59 | 0.0859
2023-12-17 13:00 | 0.0859
2023-12-17 13:01 | 0.0862
2023-12-17 13:02 | 0.086
2023-12-17 13:03 | 0.0833
2023-12-17 13:04 | 0.0764
2023-12-17 13:05 | 0.0764
2023-12-17 13:06 | 0.0764
2023-12-17 13:07 | 0.0852
2023-12-17 13:08 | 0.085
2023-12-17 13:09 | 0.0859
2023-12-17 13:10 | 0.0863
2023-12-17 13:11 | 0.0867
2023-12-17 13:12 | 0.0868
2023-12-17 13:13 | 0.0867
2023-12-17 13:14 | 0.0863
2023-12-17 13:15 | 0.0859
2023-12-17 13:16 | 0.0863
2023-12-17 13:17 | 0.086
2023-12-17 13:18 | 0.0863
2023-12-17 13:19 | 0.0862
2023-12-17 13:20 | 0.0863
2023-12-17 13:21 | 0.0863
2023-12-17 13:22 | 0.0864
2023-12-17 13:23 | 0.0864
2023-12-17 13:24 | 0.0864
2023-12-17 13:25 | 0.0865
2023-12-17 13:26 | 0.0862
2023-12-17 13:27 | 0.0859
2023-12-17 13:28 | 0.0861
2023-12-17 13:29 | 0.0863
2023-12-17 13:30 | 0.0864
2023-12-17 13:31 | 0.0864
2023-12-17 13:32 | 0.0864
2023-12-17 13:33 | 0.0866
2023-12-17 13:34 | 0.0864
2023-12-17 13:35 | 0.0863
2023-12-17 13:36 | 0.0862
2023-12-17 13:37 | 0.0862
2023-12-17 13:38 | 0.0862
2023-12-17 13:39 | 0.0863
2023-12-17 13:40 | 0.0863
2023-12-17 13:41 | 0.0864
2023-12-17 13:42 | 0.0863
2023-12-17 13:43 | 0.0864
2023-12-17 13:44 | 0.0861
2023-12-17 13:45 | 0.0862
2023-12-17 13:46 | 0.0863
2023-12-17 13:47 | 0.059
2023-12-17 13:48 | 0
2023-12-17 13:49 | 0
2023-12-17 13:50 | 0
2023-12-17 13:51 | 0
2023-12-17 13:52 | 0
2023-12-17 13:53 | 0.0307
2023-12-17 13:54 | 0.0855
2023-12-17 13:55 | 0.0859
2023-12-17 13:56 | 0.0858
2023-12-17 13:57 | 0.0859
2023-12-17 13:58 | 0.0859
2023-12-17 13:59 | 0.0859
2023-12-17 14:00 | 0.0859
2023-12-17 14:01 | 0.0859
2023-12-17 14:02 | 0.0859
2023-12-17 14:03 | 0.0861
2023-12-17 14:04 | 0.0861
2023-12-17 14:05 | 0.0863
2023-12-17 14:06 | 0.086
2023-12-17 14:07 | 0.086
2023-12-17 14:08 | 0.0859
2023-12-17 14:09 | 0.0861
2023-12-17 14:10 | 0.0861
2023-12-17 14:11 | 0.0861
2023-12-17 14:12 | 0.086
2023-12-17 14:13 | 0.086
2023-12-17 14:14 | 0.086
2023-12-17 14:15 | 0.086
2023-12-17 14:16 | 0.0861
2023-12-17 14:17 | 0.0861
2023-12-17 14:18 | 0.0862
2023-12-17 14:19 | 0.0861
2023-12-17 14:20 | 0.0863
2023-12-17 14:21 | 0.0861
2023-12-17 14:22 | 0.0861
2023-12-17 14:23 | 0.0861
2023-12-17 14:24 | 0.086
2023-12-17 14:25 | 0.086
2023-12-17 14:26 | 0.0862
2023-12-17 14:27 | 0.0861
2023-12-17 14:28 | 0.086
2023-12-17 14:29 | 0.0862
2023-12-17 14:30 | 0.0859
2023-12-17 14:31 | 0.0858
2023-12-17 14:32 | 0.086
2023-12-17 14:33 | 0.086
2023-12-17 14:34 | 0.0861
2023-12-17 14:35 | 0.0863
2023-12-17 14:36 | 0.0862
2023-12-17 14:37 | 0.0857
2023-12-17 14:38 | 0.0857
2023-12-17 14:39 | 0.0855
2023-12-17 14:40 | 0.0855
2023-12-17 14:41 | 0.0853
2023-12-17 14:42 | 0.0857
2023-12-17 14:43 | 0.0855
2023-12-17 14:44 | 0.0855
2023-12-17 14:45 | 0.0856
2023-12-17 14:46 | 0.0856
2023-12-17 14:47 | 0.0833
2023-12-17 14:48 | 0
2023-12-17 14:49 | 0
2023-12-17 14:50 | 0
2023-12-17 14:51 | 0
2023-12-17 14:52 | 0
2023-12-17 14:53 | 0.0001
2023-12-17 14:54 | 0.0905
2023-12-17 14:55 | 0.0852
2023-12-17 14:56 | 0.0856
2023-12-17 14:57 | 0.0855
2023-12-17 14:58 | 0.0855
2023-12-17 14:59 | 0.0855
2023-12-17 15:00 | 0.0857
2023-12-17 15:01 | 0.0855
2023-12-17 15:02 | 0.0857
2023-12-17 15:03 | 0.0856
2023-12-17 15:04 | 0.0855
2023-12-17 15:05 | 0.0858
2023-12-17 15:06 | 0.0859
2023-12-17 15:07 | 0.0857
2023-12-17 15:08 | 0.0858
2023-12-17 15:09 | 0.0859
2023-12-17 15:10 | 0.0856
2023-12-17 15:11 | 0.0859
2023-12-17 15:12 | 0.0859
2023-12-17 15:13 | 0.0857
2023-12-17 15:14 | 0.0858
2023-12-17 15:15 | 0.0858
2023-12-17 15:16 | 0.0859
2023-12-17 15:17 | 0.0858
2023-12-17 15:18 | 0.0859
2023-12-17 15:19 | 0.0859
2023-12-17 15:20 | 0.0859
2023-12-17 15:21 | 0.086
2023-12-17 15:22 | 0.0859
2023-12-17 15:23 | 0.0858
2023-12-17 15:24 | 0.0858
2023-12-17 15:25 | 0.0859
2023-12-17 15:26 | 0.0859
2023-12-17 15:27 | 0.0861
2023-12-17 15:28 | 0.0859
2023-12-17 15:29 | 0.086
2023-12-17 15:30 | 0.0859
2023-12-17 15:31 | 0.0858
2023-12-17 15:32 | 0.0859
2023-12-17 15:33 | 0.086
2023-12-17 15:34 | 0.0859
2023-12-17 15:35 | 0.086
2023-12-17 15:36 | 0.0861
2023-12-17 15:37 | 0.0859
2023-12-17 15:38 | 0.0861
2023-12-17 15:39 | 0.0859
2023-12-17 15:40 | 0.0857
2023-12-17 15:41 | 0.0857
2023-12-17 15:42 | 0.0857
2023-12-17 15:43 | 0.0858
2023-12-17 15:44 | 0.0858
2023-12-17 15:45 | 0.0857
2023-12-17 15:46 | 0.0857
2023-12-17 15:47 | 0.0856
2023-12-17 15:48 | 0.0259
2023-12-17 15:49 | 0
2023-12-17 15:50 | 0
2023-12-17 15:51 | 0
2023-12-17 15:52 | 0
2023-12-17 15:53 | 0
2023-12-17 15:54 | 0.0627
2023-12-17 15:55 | 0.0851
2023-12-17 15:56 | 0.0852
2023-12-17 15:57 | 0.0854
2023-12-17 15:58 | 0.0855
2023-12-17 15:59 | 0.0855
2023-12-17 16:00 | 0.0856
2023-12-17 16:01 | 0.0858
2023-12-17 16:02 | 0.0856
2023-12-17 16:03 | 0.0857
2023-12-17 16:04 | 0.0858
2023-12-17 16:05 | 0.0856
2023-12-17 16:06 | 0.0857
2023-12-17 16:07 | 0.0856
2023-12-17 16:08 | 0.0857
2023-12-17 16:09 | 0.0858
2023-12-17 16:10 | 0.0859
2023-12-17 16:11 | 0.0857
2023-12-17 16:12 | 0.0859
2023-12-17 16:13 | 0.0859
2023-12-17 16:14 | 0.086
2023-12-17 16:15 | 0.0859
2023-12-17 16:16 | 0.0858
2023-12-17 16:17 | 0.0856
2023-12-17 16:18 | 0.0857
2023-12-17 16:19 | 0.0856
2023-12-17 16:20 | 0.0855
2023-12-17 16:21 | 0.0855
2023-12-17 16:22 | 0.0852
2023-12-17 16:23 | 0.0855
2023-12-17 16:24 | 0.0854
2023-12-17 16:25 | 0.0855
2023-12-17 16:26 | 0.0855
2023-12-17 16:27 | 0.0854
2023-12-17 16:28 | 0.0854
2023-12-17 16:29 | 0.0856
2023-12-17 16:30 | 0.0856
2023-12-17 16:31 | 0.0856
2023-12-17 16:32 | 0.0856
2023-12-17 16:33 | 0.0856
2023-12-17 16:34 | 0.0855
2023-12-17 16:35 | 0.0854
2023-12-17 16:36 | 0.0855
2023-12-17 16:37 | 0.0854
2023-12-17 16:38 | 0.0853
2023-12-17 16:39 | 0.0853
2023-12-17 16:40 | 0.0857
2023-12-17 16:41 | 0.0854
2023-12-17 16:42 | 0.0854
2023-12-17 16:43 | 0.0854
2023-12-17 16:44 | 0.0856
2023-12-17 16:45 | 0.0853
2023-12-17 16:46 | 0.0855
2023-12-17 16:47 | 0.0855
2023-12-17 16:48 | 0.0541
2023-12-17 16:49 | 0
2023-12-17 16:50 | 0
2023-12-17 16:51 | 0
2023-12-17 16:52 | 0
2023-12-17 16:53 | 0
2023-12-17 16:54 | 0.0344
2023-12-17 16:55 | 0.0851
2023-12-17 16:56 | 0.0852
2023-12-17 16:57 | 0.085
2023-12-17 16:58 | 0.0851
2023-12-17 16:59 | 0.0851
2023-12-17 17:00 | 0.085
2023-12-17 17:01 | 0.0852
2023-12-17 17:02 | 0.0851
2023-12-17 17:03 | 0.0851
2023-12-17 17:04 | 0.0853
2023-12-17 17:05 | 0.0852
2023-12-17 17:06 | 0.0853
2023-12-17 17:07 | 0.0854
2023-12-17 17:08 | 0.0854
2023-12-17 17:09 | 0.0855
2023-12-17 17:10 | 0.0853
2023-12-17 17:11 | 0.0851
2023-12-17 17:12 | 0.0855
2023-12-17 17:13 | 0.0852
2023-12-17 17:14 | 0.0852
2023-12-17 17:15 | 0.0852
2023-12-17 17:16 | 0.0852
2023-12-17 17:17 | 0.0851
2023-12-17 17:18 | 0.0851
2023-12-17 17:19 | 0.0854
2023-12-17 17:20 | 0.0854
2023-12-17 17:21 | 0.0851
2023-12-17 17:22 | 0.0852
2023-12-17 17:23 | 0.0854
2023-12-17 17:24 | 0.0853
2023-12-17 17:25 | 0.0852
2023-12-17 17:26 | 0.0853
2023-12-17 17:27 | 0.0853
2023-12-17 17:28 | 0.0853
2023-12-17 17:29 | 0.0852
2023-12-17 17:30 | 0.0852
2023-12-17 17:31 | 0.0852
2023-12-17 17:32 | 0.0851
2023-12-17 17:33 | 0.085
2023-12-17 17:34 | 0.0849
2023-12-17 17:35 | 0.0848
2023-12-17 17:36 | 0.0852
2023-12-17 17:37 | 0.0853
2023-12-17 17:38 | 0.0852
2023-12-17 17:39 | 0.0851
2023-12-17 17:40 | 0.0852
2023-12-17 17:41 | 0.0851
2023-12-17 17:42 | 0.0852
2023-12-17 17:43 | 0.0852
2023-12-17 17:44 | 0.0851
2023-12-17 17:45 | 0.0851
2023-12-17 17:46 | 0.0853
2023-12-17 17:47 | 0.0853
2023-12-17 17:48 | 0.0824
2023-12-17 17:49 | 0
2023-12-17 17:50 | 0
2023-12-17 17:51 | 0
2023-12-17 17:52 | 0
2023-12-17 17:53 | 0
2023-12-17 17:54 | 0.0013
2023-12-17 17:55 | 0.0894
2023-12-17 17:56 | 0.0848
2023-12-17 17:57 | 0.0851
2023-12-17 17:58 | 0.0852
2023-12-17 17:59 | 0.0854
2023-12-17 18:00 | 0.0854
2023-12-17 18:01 | 0.0853
2023-12-17 18:02 | 0.0852
2023-12-17 18:03 | 0.0853
2023-12-17 18:04 | 0.0855
2023-12-17 18:05 | 0.0855
2023-12-17 18:06 | 0.0852
2023-12-17 18:07 | 0.0853
2023-12-17 18:08 | 0.0853
2023-12-17 18:09 | 0.0853
2023-12-17 18:10 | 0.0853
2023-12-17 18:11 | 0.0853
2023-12-17 18:12 | 0.0852
2023-12-17 18:13 | 0.0856
2023-12-17 18:14 | 0.0855
2023-12-17 18:15 | 0.0855
2023-12-17 18:16 | 0.0855
2023-12-17 18:17 | 0.0857
2023-12-17 18:18 | 0.0854
2023-12-17 18:19 | 0.0854
2023-12-17 18:20 | 0.0855
2023-12-17 18:21 | 0.0854
2023-12-17 18:22 | 0.0854
2023-12-17 18:23 | 0.0853
2023-12-17 18:24 | 0.0854
2023-12-17 18:25 | 0.0855
2023-12-17 18:26 | 0.0852
2023-12-17 18:27 | 0.0852
2023-12-17 18:28 | 0.0853
2023-12-17 18:29 | 0.0855
2023-12-17 18:30 | 0.0851
2023-12-17 18:31 | 0.0853
2023-12-17 18:32 | 0.0853
2023-12-17 18:33 | 0.0854
2023-12-17 18:34 | 0.0854
2023-12-17 18:35 | 0.0853
2023-12-17 18:36 | 0.0855
2023-12-17 18:37 | 0.0852
2023-12-17 18:38 | 0.0843
2023-12-17 18:39 | 0.0842
2023-12-17 18:40 | 0.0849
2023-12-17 18:41 | 0.0851
2023-12-17 18:42 | 0.0851
2023-12-17 18:43 | 0.0851
2023-12-17 18:44 | 0.0851
2023-12-17 18:45 | 0.085
2023-12-17 18:46 | 0.0851
2023-12-17 18:47 | 0.0851
2023-12-17 18:48 | 0.0851
2023-12-17 18:49 | 0.025
2023-12-17 18:50 | 0
2023-12-17 18:51 | 0
2023-12-17 18:52 | 0
2023-12-17 18:53 | 0
2023-12-17 18:54 | 0
2023-12-17 18:55 | 0.0631
2023-12-17 18:56 | 0.0851
2023-12-17 18:57 | 0.0852
2023-12-17 18:58 | 0.0851
2023-12-17 18:59 | 0.0852
2023-12-17 19:00 | 0.0851
2023-12-17 19:01 | 0.0853
2023-12-17 19:02 | 0.0854
2023-12-17 19:03 | 0.0853
2023-12-17 19:04 | 0.0853
2023-12-17 19:05 | 0.0853
2023-12-17 19:06 | 0.0854
2023-12-17 19:07 | 0.0854
2023-12-17 19:08 | 0.0854
2023-12-17 19:09 | 0.0849
2023-12-17 19:10 | 0.085
2023-12-17 19:11 | 0.0852
2023-12-17 19:12 | 0.0853
2023-12-17 19:13 | 0.0851
2023-12-17 19:14 | 0.0853
2023-12-17 19:15 | 0.0854
2023-12-17 19:16 | 0.0852
2023-12-17 19:17 | 0.0854
2023-12-17 19:18 | 0.0856
2023-12-17 19:19 | 0.0856
2023-12-17 19:20 | 0.0857
2023-12-17 19:21 | 0.0862
2023-12-17 19:22 | 0.086
2023-12-17 19:23 | 0.086
2023-12-17 19:24 | 0.0858
2023-12-17 19:25 | 0.0854
2023-12-17 19:26 | 0.0842
2023-12-17 19:27 | 0.0839
2023-12-17 19:28 | 0.0846
2023-12-17 19:29 | 0.0849
2023-12-17 19:30 | 0.0853
2023-12-17 19:31 | 0.0842
2023-12-17 19:32 | 0.0838
2023-12-17 19:33 | 0.0835
2023-12-17 19:34 | 0.0836
2023-12-17 19:35 | 0.0835
2023-12-17 19:36 | 0.0836
2023-12-17 19:37 | 0.0836
2023-12-17 19:38 | 0.0835
2023-12-17 19:39 | 0.0838
2023-12-17 19:40 | 0.0837
2023-12-17 19:41 | 0.0835
2023-12-17 19:42 | 0.0836
2023-12-17 19:43 | 0.0836
2023-12-17 19:44 | 0.0843
2023-12-17 19:45 | 0.0853
2023-12-17 19:46 | 0.0853
2023-12-17 19:47 | 0.0854
2023-12-17 19:48 | 0.0846
2023-12-17 19:49 | 0.0838
2023-12-17 19:50 | 0.0845
2023-12-17 19:51 | 0.0852
2023-12-17 19:52 | 0.0853
2023-12-17 19:53 | 0.0844
2023-12-17 19:54 | 0.0203
2023-12-17 19:55 | 0.037
2023-12-17 19:56 | 0.0834
2023-12-17 19:57 | 0.0836
2023-12-17 19:58 | 0.0838
2023-12-17 19:59 | 0.0838
2023-12-17 20:00 | 0.0838
2023-12-17 20:01 | 0.0835
2023-12-17 20:02 | 0.0836
2023-12-17 20:03 | 0.0836
2023-12-17 20:04 | 0.0838
2023-12-17 20:05 | 0.0837
2023-12-17 20:06 | 0.0838
2023-12-17 20:07 | 0.084
2023-12-17 20:08 | 0.084
2023-12-17 20:09 | 0.0842
2023-12-17 20:10 | 0.0842
2023-12-17 20:11 | 0.0839
2023-12-17 20:12 | 0.0839
2023-12-17 20:13 | 0.0836
2023-12-17 20:14 | 0.0834
2023-12-17 20:15 | 0.0835
2023-12-17 20:16 | 0.0841
2023-12-17 20:17 | 0.0849
2023-12-17 20:18 | 0.0847
2023-12-17 20:19 | 0.0848
2023-12-17 20:20 | 0.0848
2023-12-17 20:21 | 0.0849
2023-12-17 20:22 | 0.0849
2023-12-17 20:23 | 0.0852
2023-12-17 20:24 | 0.085
2023-12-17 20:25 | 0.085
2023-12-17 20:26 | 0.085
2023-12-17 20:27 | 0.085
2023-12-17 20:28 | 0.0851
2023-12-17 20:29 | 0.0852
2023-12-17 20:30 | 0.0852
2023-12-17 20:31 | 0.0853
2023-12-17 20:32 | 0.0852
2023-12-17 20:33 | 0.0852
2023-12-17 20:34 | 0.0852
2023-12-17 20:35 | 0.085
2023-12-17 20:36 | 0.0851
2023-12-17 20:37 | 0.085
2023-12-17 20:38 | 0.0852
2023-12-17 20:39 | 0.0851
2023-12-17 20:40 | 0.085
2023-12-17 20:41 | 0.085
2023-12-17 20:42 | 0.0852
2023-12-17 20:43 | 0.085
2023-12-17 20:44 | 0.085
2023-12-17 20:45 | 0.0851
2023-12-17 20:46 | 0.0849
2023-12-17 20:47 | 0.0849
2023-12-17 20:48 | 0.0849
2023-12-17 20:49 | 0.0723
2023-12-17 20:50 | 0
2023-12-17 20:51 | 0
2023-12-17 20:52 | 0
2023-12-17 20:53 | 0
2023-12-17 20:54 | 0
2023-12-17 20:55 | 0.0167
2023-12-17 20:56 | 0.0842
2023-12-17 20:57 | 0.0846
2023-12-17 20:58 | 0.0847
2023-12-17 20:59 | 0.0846
2023-12-17 21:00 | 0.0846
2023-12-17 21:01 | 0.0847
2023-12-17 21:02 | 0.0846
2023-12-17 21:03 | 0.0847
2023-12-17 21:04 | 0.0846
2023-12-17 21:05 | 0.0848
2023-12-17 21:06 | 0.0848
2023-12-17 21:07 | 0.0847
2023-12-17 21:08 | 0.0847
2023-12-17 21:09 | 0.0848
2023-12-17 21:10 | 0.0851
2023-12-17 21:11 | 0.0849
2023-12-17 21:12 | 0.0848
2023-12-17 21:13 | 0.0847
2023-12-17 21:14 | 0.0848
2023-12-17 21:15 | 0.0848
2023-12-17 21:16 | 0.085
2023-12-17 21:17 | 0.085
2023-12-17 21:18 | 0.0851
2023-12-17 21:19 | 0.0849
2023-12-17 21:20 | 0.085
2023-12-17 21:21 | 0.0852
2023-12-17 21:22 | 0.0852
2023-12-17 21:23 | 0.0852
2023-12-17 21:24 | 0.085
2023-12-17 21:25 | 0.0852
2023-12-17 21:26 | 0.0853
2023-12-17 21:27 | 0.0853
2023-12-17 21:28 | 0.0854
2023-12-17 21:29 | 0.0852
2023-12-17 21:30 | 0.0852
2023-12-17 21:31 | 0.0853
2023-12-17 21:32 | 0.0851
2023-12-17 21:33 | 0.0853
2023-12-17 21:34 | 0.0854
2023-12-17 21:35 | 0.0854
2023-12-17 21:36 | 0.0852
2023-12-17 21:37 | 0.0852
2023-12-17 21:38 | 0.0852
2023-12-17 21:39 | 0.0854
2023-12-17 21:40 | 0.0853
2023-12-17 21:41 | 0.0854
2023-12-17 21:42 | 0.0854
2023-12-17 21:43 | 0.0857
2023-12-17 21:44 | 0.0855
2023-12-17 21:45 | 0.0853
2023-12-17 21:46 | 0.0854
2023-12-17 21:47 | 0.0852
2023-12-17 21:48 | 0.0852
2023-12-17 21:49 | 0.0853
2023-12-17 21:50 | 0.0039
2023-12-17 21:51 | 0
2023-12-17 21:52 | 0
2023-12-17 21:53 | 0
2023-12-17 21:54 | 0
2023-12-17 21:55 | 0
2023-12-17 21:56 | 0.0856
2023-12-17 21:57 | 0.085
2023-12-17 21:58 | 0.0853
2023-12-17 21:59 | 0.0854
2023-12-17 22:00 | 0.0854
2023-12-17 22:01 | 0.0854
2023-12-17 22:02 | 0.0855
2023-12-17 22:03 | 0.0853
2023-12-17 22:04 | 0.0855
2023-12-17 22:05 | 0.0853
2023-12-17 22:06 | 0.0854
2023-12-17 22:07 | 0.0855
2023-12-17 22:08 | 0.0856
2023-12-17 22:09 | 0.0854
2023-12-17 22:10 | 0.0854
2023-12-17 22:11 | 0.0856
2023-12-17 22:12 | 0.0856
2023-12-17 22:13 | 0.0856
2023-12-17 22:14 | 0.0855
2023-12-17 22:15 | 0.0856
2023-12-17 22:16 | 0.0857
2023-12-17 22:17 | 0.0854
2023-12-17 22:18 | 0.0855
2023-12-17 22:19 | 0.0855
2023-12-17 22:20 | 0.0855
2023-12-17 22:21 | 0.0852
2023-12-17 22:22 | 0.0853
2023-12-17 22:23 | 0.0855
2023-12-17 22:24 | 0.0855
2023-12-17 22:25 | 0.0855
2023-12-17 22:26 | 0.0853
2023-12-17 22:27 | 0.0853
2023-12-17 22:28 | 0.0855
2023-12-17 22:29 | 0.0853
2023-12-17 22:30 | 0.0853
2023-12-17 22:31 | 0.0854
2023-12-17 22:32 | 0.0853
2023-12-17 22:33 | 0.0852
2023-12-17 22:34 | 0.0855
2023-12-17 22:35 | 0.0853
2023-12-17 22:36 | 0.0853
2023-12-17 22:37 | 0.0855
2023-12-17 22:38 | 0.0852
2023-12-17 22:39 | 0.0851
2023-12-17 22:40 | 0.0851
2023-12-17 22:41 | 0.0851
2023-12-17 22:42 | 0.0852
2023-12-17 22:43 | 0.0852
2023-12-17 22:44 | 0.0853
2023-12-17 22:45 | 0.0853
2023-12-17 22:46 | 0.0854
2023-12-17 22:47 | 0.0852
2023-12-17 22:48 | 0.0854
2023-12-17 22:49 | 0.0855
2023-12-17 22:50 | 0.0175
2023-12-17 22:51 | 0
2023-12-17 22:52 | 0
2023-12-17 22:53 | 0
2023-12-17 22:54 | 0
2023-12-17 22:55 | 0
2023-12-17 22:56 | 0.0724
2023-12-17 22:57 | 0.0851
2023-12-17 22:58 | 0.085
2023-12-17 22:59 | 0.0851
2023-12-17 23:00 | 0.0849
2023-12-17 23:01 | 0.0851
2023-12-17 23:02 | 0.0851
2023-12-17 23:03 | 0.085
2023-12-17 23:04 | 0.0851
2023-12-17 23:05 | 0.0851
2023-12-17 23:06 | 0.085
2023-12-17 23:07 | 0.0852
2023-12-17 23:08 | 0.0853
2023-12-17 23:09 | 0.0855
2023-12-17 23:10 | 0.0852
2023-12-17 23:11 | 0.0851
2023-12-17 23:12 | 0.0852
2023-12-17 23:13 | 0.0851
2023-12-17 23:14 | 0.085
2023-12-17 23:15 | 0.085
2023-12-17 23:16 | 0.0851
2023-12-17 23:17 | 0.0851
2023-12-17 23:18 | 0.0851
2023-12-17 23:19 | 0.085
2023-12-17 23:20 | 0.0852
2023-12-17 23:21 | 0.0852
2023-12-17 23:22 | 0.085
2023-12-17 23:23 | 0.0851
2023-12-17 23:24 | 0.0851
2023-12-17 23:25 | 0.0852
2023-12-17 23:26 | 0.0853
2023-12-17 23:27 | 0.0851
2023-12-17 23:28 | 0.0854
2023-12-17 23:29 | 0.0854
2023-12-17 23:30 | 0.0853
2023-12-17 23:31 | 0.0855
2023-12-17 23:32 | 0.0853
2023-12-17 23:33 | 0.0854
2023-12-17 23:34 | 0.0855
2023-12-17 23:35 | 0.0852
2023-12-17 23:36 | 0.0853
2023-12-17 23:37 | 0.0851
2023-12-17 23:38 | 0.085
2023-12-17 23:39 | 0.0851
2023-12-17 23:40 | 0.0851
2023-12-17 23:41 | 0.0851
2023-12-17 23:42 | 0.0853
2023-12-17 23:43 | 0.0854
2023-12-17 23:44 | 0.0854
2023-12-17 23:45 | 0.0853
2023-12-17 23:46 | 0.0853
2023-12-17 23:47 | 0.0853
2023-12-17 23:48 | 0.0854
2023-12-17 23:49 | 0.0853
2023-12-17 23:50 | 0.0285
2023-12-17 23:51 | 0
2023-12-17 23:52 | 0
2023-12-17 23:53 | 0
2023-12-17 23:54 | 0
2023-12-17 23:55 | 0
2023-12-17 23:56 | 0.0616
2023-12-17 23:57 | 0.0851
2023-12-17 23:58 | 0.0852
2023-12-17 23:59 | 0.085
2023-12-18 | 0.0851
2023-12-18 00:01 | 0.0853
2023-12-18 00:02 | 0.0853
2023-12-18 00:03 | 0.0853
2023-12-18 00:04 | 0.0854
2023-12-18 00:05 | 0.0855
2023-12-18 00:06 | 0.0852
2023-12-18 00:07 | 0.0855
2023-12-18 00:08 | 0.0855
2023-12-18 00:09 | 0.0854
2023-12-18 00:10 | 0.0856
2023-12-18 00:11 | 0.0854
2023-12-18 00:12 | 0.0856
2023-12-18 00:13 | 0.0852
2023-12-18 00:14 | 0.0854
2023-12-18 00:15 | 0.0854
2023-12-18 00:16 | 0.0852
2023-12-18 00:17 | 0.0854
2023-12-18 00:18 | 0.0855
2023-12-18 00:19 | 0.0855
2023-12-18 00:20 | 0.0854
2023-12-18 00:21 | 0.0854
2023-12-18 00:22 | 0.0854
2023-12-18 00:23 | 0.0853
2023-12-18 00:24 | 0.0858
2023-12-18 00:25 | 0.0856
2023-12-18 00:26 | 0.0855
2023-12-18 00:27 | 0.0855
2023-12-18 00:28 | 0.0857
2023-12-18 00:29 | 0.0854
2023-12-18 00:30 | 0.0853
2023-12-18 00:31 | 0.0854
2023-12-18 00:32 | 0.0853
2023-12-18 00:33 | 0.0855
2023-12-18 00:34 | 0.0856
2023-12-18 00:35 | 0.0855
2023-12-18 00:36 | 0.0855
2023-12-18 00:37 | 0.0857
2023-12-18 00:38 | 0.0856
2023-12-18 00:39 | 0.0856
2023-12-18 00:40 | 0.0855
2023-12-18 00:41 | 0.0856
2023-12-18 00:42 | 0.0858
2023-12-18 00:43 | 0.0855
2023-12-18 00:44 | 0.0855
2023-12-18 00:45 | 0.0855
2023-12-18 00:46 | 0.0857
2023-12-18 00:47 | 0.0857
2023-12-18 00:48 | 0.0858
2023-12-18 00:49 | 0.0857
2023-12-18 00:50 | 0.0385
2023-12-18 00:51 | 0
2023-12-18 00:52 | 0
2023-12-18 00:53 | 0
2023-12-18 00:54 | 0
2023-12-18 00:55 | 0
2023-12-18 00:56 | 0.052
2023-12-18 00:57 | 0.0852
2023-12-18 00:58 | 0.0854
2023-12-18 00:59 | 0.0855
2023-12-18 01:00 | 0.0857
2023-12-18 01:01 | 0.0854
2023-12-18 01:02 | 0.0854
2023-12-18 01:03 | 0.0855
2023-12-18 01:04 | 0.0856
2023-12-18 01:05 | 0.0855
2023-12-18 01:06 | 0.0855
2023-12-18 01:07 | 0.0856
2023-12-18 01:08 | 0.0856
2023-12-18 01:09 | 0.0854
2023-12-18 01:10 | 0.0855
2023-12-18 01:11 | 0.0856
2023-12-18 01:12 | 0.0856
2023-12-18 01:13 | 0.0857
2023-12-18 01:14 | 0.0856
2023-12-18 01:15 | 0.0858
2023-12-18 01:16 | 0.0856
2023-12-18 01:17 | 0.0856
2023-12-18 01:18 | 0.0856
2023-12-18 01:19 | 0.0857
2023-12-18 01:20 | 0.0856
2023-12-18 01:21 | 0.0856
2023-12-18 01:22 | 0.0856
2023-12-18 01:23 | 0.0856
2023-12-18 01:24 | 0.0855
2023-12-18 01:25 | 0.0851
2023-12-18 01:26 | 0.085
2023-12-18 01:27 | 0.0849
2023-12-18 01:28 | 0.0853
2023-12-18 01:29 | 0.0849
2023-12-18 01:30 | 0.0851
2023-12-18 01:31 | 0.0851
2023-12-18 01:32 | 0.0849
2023-12-18 01:33 | 0.085
2023-12-18 01:34 | 0.0848
2023-12-18 01:35 | 0.0849
2023-12-18 01:36 | 0.0849
2023-12-18 01:37 | 0.0848
2023-12-18 01:38 | 0.0849
2023-12-18 01:39 | 0.0847
2023-12-18 01:40 | 0.0847
2023-12-18 01:41 | 0.0847
2023-12-18 01:42 | 0.0848
2023-12-18 01:43 | 0.0848
2023-12-18 01:44 | 0.085
2023-12-18 01:45 | 0.0849
2023-12-18 01:46 | 0.0849
2023-12-18 01:47 | 0.085
2023-12-18 01:48 | 0.0849
2023-12-18 01:49 | 0.085
2023-12-18 01:50 | 0.0474
2023-12-18 01:51 | 0
2023-12-18 01:52 | 0
2023-12-18 01:53 | 0
2023-12-18 01:54 | 0
2023-12-18 01:55 | 0
2023-12-18 01:56 | 0.043
2023-12-18 01:57 | 0.0848
2023-12-18 01:58 | 0.085
2023-12-18 01:59 | 0.0849
2023-12-18 02:00 | 0.0849
2023-12-18 02:01 | 0.0849
2023-12-18 02:02 | 0.085
2023-12-18 02:03 | 0.085
2023-12-18 02:04 | 0.0849
2023-12-18 02:05 | 0.0848
2023-12-18 02:06 | 0.0849
2023-12-18 02:07 | 0.0847
2023-12-18 02:08 | 0.0849
2023-12-18 02:09 | 0.085
2023-12-18 02:10 | 0.0849
2023-12-18 02:11 | 0.0853
2023-12-18 02:12 | 0.0849
2023-12-18 02:13 | 0.0848
2023-12-18 02:14 | 0.0848
2023-12-18 02:15 | 0.0848
2023-12-18 02:16 | 0.0848
2023-12-18 02:17 | 0.0849
2023-12-18 02:18 | 0.085
2023-12-18 02:19 | 0.0854
2023-12-18 02:20 | 0.085
2023-12-18 02:21 | 0.085
2023-12-18 02:22 | 0.0851
2023-12-18 02:23 | 0.0848
2023-12-18 02:24 | 0.0849
2023-12-18 02:25 | 0.0851
2023-12-18 02:26 | 0.0851
2023-12-18 02:27 | 0.085
2023-12-18 02:28 | 0.0853
2023-12-18 02:29 | 0.0851
2023-12-18 02:30 | 0.0849
2023-12-18 02:31 | 0.0849
2023-12-18 02:32 | 0.0849
2023-12-18 02:33 | 0.0849
2023-12-18 02:34 | 0.0848
2023-12-18 02:35 | 0.0849
2023-12-18 02:36 | 0.0848
2023-12-18 02:37 | 0.0849
2023-12-18 02:38 | 0.0848
2023-12-18 02:39 | 0.0847
2023-12-18 02:40 | 0.0848
2023-12-18 02:41 | 0.085
2023-12-18 02:42 | 0.085
2023-12-18 02:43 | 0.0847
2023-12-18 02:44 | 0.0847
2023-12-18 02:45 | 0.0848
2023-12-18 02:46 | 0.0849
2023-12-18 02:47 | 0.0849
2023-12-18 02:48 | 0.0848
2023-12-18 02:49 | 0.0847
2023-12-18 02:50 | 0.0534
2023-12-18 02:51 | 0
2023-12-18 02:52 | 0
2023-12-18 02:53 | 0
2023-12-18 02:54 | 0
2023-12-18 02:55 | 0
2023-12-18 02:56 | 0.0366
2023-12-18 02:57 | 0.0842
2023-12-18 02:58 | 0.0845
2023-12-18 02:59 | 0.0846
2023-12-18 03:00 | 0.0846
2023-12-18 03:01 | 0.0849
2023-12-18 03:02 | 0.0849
2023-12-18 03:03 | 0.0848
2023-12-18 03:04 | 0.0849
2023-12-18 03:05 | 0.0849
2023-12-18 03:06 | 0.0851
2023-12-18 03:07 | 0.0851
2023-12-18 03:08 | 0.0848
2023-12-18 03:09 | 0.0848
2023-12-18 03:10 | 0.0847
2023-12-18 03:11 | 0.0848
2023-12-18 03:12 | 0.0847
2023-12-18 03:13 | 0.0853
2023-12-18 03:14 | 0.085
2023-12-18 03:15 | 0.085
2023-12-18 03:16 | 0.085
2023-12-18 03:17 | 0.085
2023-12-18 03:18 | 0.0849
2023-12-18 03:19 | 0.0848
2023-12-18 03:20 | 0.085
2023-12-18 03:21 | 0.085
2023-12-18 03:22 | 0.0849
2023-12-18 03:23 | 0.0848
2023-12-18 03:24 | 0.0849
2023-12-18 03:25 | 0.0847
2023-12-18 03:26 | 0.0847
2023-12-18 03:27 | 0.0848
2023-12-18 03:28 | 0.085
2023-12-18 03:29 | 0.0849
2023-12-18 03:30 | 0.0848
2023-12-18 03:31 | 0.0849
2023-12-18 03:32 | 0.0847
2023-12-18 03:33 | 0.0846
2023-12-18 03:34 | 0.085
2023-12-18 03:35 | 0.0848
2023-12-18 03:36 | 0.085
2023-12-18 03:37 | 0.0847
2023-12-18 03:38 | 0.0848
2023-12-18 03:39 | 0.0848
2023-12-18 03:40 | 0.0849
2023-12-18 03:41 | 0.0848
2023-12-18 03:42 | 0.0847
2023-12-18 03:43 | 0.0847
2023-12-18 03:44 | 0.0849
2023-12-18 03:45 | 0.0848
2023-12-18 03:46 | 0.0849
2023-12-18 03:47 | 0.0852
2023-12-18 03:48 | 0.0851
2023-12-18 03:49 | 0.0849
2023-12-18 03:50 | 0.0587
2023-12-18 03:51 | 0
2023-12-18 03:52 | 0
2023-12-18 03:53 | 0
2023-12-18 03:54 | 0
2023-12-18 03:55 | 0
2023-12-18 03:56 | 0.0313
2023-12-18 03:57 | 0.0841
2023-12-18 03:58 | 0.0844
2023-12-18 03:59 | 0.0846
2023-12-18 04:00 | 0.0846
2023-12-18 04:01 | 0.0845
2023-12-18 04:02 | 0.0844
2023-12-18 04:03 | 0.0843
2023-12-18 04:04 | 0.0846
2023-12-18 04:05 | 0.0846
2023-12-18 04:06 | 0.0844
2023-12-18 04:07 | 0.0846
2023-12-18 04:08 | 0.0846
2023-12-18 04:09 | 0.0846
2023-12-18 04:10 | 0.0846
2023-12-18 04:11 | 0.0846
2023-12-18 04:12 | 0.0845
2023-12-18 04:13 | 0.0847
2023-12-18 04:14 | 0.0847
2023-12-18 04:15 | 0.0846
2023-12-18 04:16 | 0.0846
2023-12-18 04:17 | 0.0846
2023-12-18 04:18 | 0.0847
2023-12-18 04:19 | 0.0845
2023-12-18 04:20 | 0.0845
2023-12-18 04:21 | 0.0844
2023-12-18 04:22 | 0.0848
2023-12-18 04:23 | 0.0851
2023-12-18 04:24 | 0.085
2023-12-18 04:25 | 0.0848
2023-12-18 04:26 | 0.0849
2023-12-18 04:27 | 0.0849
2023-12-18 04:28 | 0.0845
2023-12-18 04:29 | 0.0844
2023-12-18 04:30 | 0.0843
2023-12-18 04:31 | 0.0845
2023-12-18 04:32 | 0.0845
2023-12-18 04:33 | 0.0846
2023-12-18 04:34 | 0.0842
2023-12-18 04:35 | 0.0837
2023-12-18 04:36 | 0.0837
2023-12-18 04:37 | 0.0842
2023-12-18 04:38 | 0.0845
2023-12-18 04:39 | 0.0844
2023-12-18 04:40 | 0.0843
2023-12-18 04:41 | 0.0841
2023-12-18 04:42 | 0.0843
2023-12-18 04:43 | 0.0843
2023-12-18 04:44 | 0.0838
2023-12-18 04:45 | 0.0842
2023-12-18 04:46 | 0.0844
2023-12-18 04:47 | 0.0848
2023-12-18 04:48 | 0.0848
2023-12-18 04:49 | 0.0846
2023-12-18 04:50 | 0.0634
2023-12-18 04:51 | 0
2023-12-18 04:52 | 0
2023-12-18 04:53 | 0
2023-12-18 04:54 | 0
2023-12-18 04:55 | 0
2023-12-18 04:56 | 0.0279
2023-12-18 04:57 | 0.0845
2023-12-18 04:58 | 0.0838
2023-12-18 04:59 | 0.0846
2023-12-18 05:00 | 0.0844
2023-12-18 05:01 | 0.0846
2023-12-18 05:02 | 0.0851
2023-12-18 05:03 | 0.0849
2023-12-18 05:04 | 0.0849
2023-12-18 05:05 | 0.085
2023-12-18 05:06 | 0.085
2023-12-18 05:07 | 0.0851
2023-12-18 05:08 | 0.0848
2023-12-18 05:09 | 0.0851
2023-12-18 05:10 | 0.0849
2023-12-18 05:11 | 0.0851
2023-12-18 05:12 | 0.0852
2023-12-18 05:13 | 0.0851
2023-12-18 05:14 | 0.0852
2023-12-18 05:15 | 0.0852
2023-12-18 05:16 | 0.0853
2023-12-18 05:17 | 0.0851
2023-12-18 05:18 | 0.0851
2023-12-18 05:19 | 0.0849
2023-12-18 05:20 | 0.085
2023-12-18 05:21 | 0.085
2023-12-18 05:22 | 0.0848
2023-12-18 05:23 | 0.0851
2023-12-18 05:24 | 0.0849
2023-12-18 05:25 | 0.0851
2023-12-18 05:26 | 0.0852
2023-12-18 05:27 | 0.0852
2023-12-18 05:28 | 0.0851
2023-12-18 05:29 | 0.085
2023-12-18 05:30 | 0.0851
2023-12-18 05:31 | 0.0851
2023-12-18 05:32 | 0.085
2023-12-18 05:33 | 0.085
2023-12-18 05:34 | 0.0851
2023-12-18 05:35 | 0.0852
2023-12-18 05:36 | 0.085
2023-12-18 05:37 | 0.0852
2023-12-18 05:38 | 0.0852
2023-12-18 05:39 | 0.0854
2023-12-18 05:40 | 0.0853
2023-12-18 05:41 | 0.0851
2023-12-18 05:42 | 0.085
2023-12-18 05:43 | 0.0851
2023-12-18 05:44 | 0.0852
2023-12-18 05:45 | 0.0848
2023-12-18 05:46 | 0.0846
2023-12-18 05:47 | 0.0847
2023-12-18 05:48 | 0.0845
2023-12-18 05:49 | 0.0849
2023-12-18 05:50 | 0.0693
2023-12-18 05:51 | 0
2023-12-18 05:52 | 0
2023-12-18 05:53 | 0
2023-12-18 05:54 | 0
2023-12-18 05:55 | 0
2023-12-18 05:56 | 0.0219
2023-12-18 05:57 | 0.0845
2023-12-18 05:58 | 0.0844
2023-12-18 05:59 | 0.0846
2023-12-18 06:00 | 0.0842
2023-12-18 06:01 | 0.084
2023-12-18 06:02 | 0.0844
2023-12-18 06:03 | 0.0845
2023-12-18 06:04 | 0.0842
2023-12-18 06:05 | 0.0839
2023-12-18 06:06 | 0.0843
2023-12-18 06:07 | 0.0842
2023-12-18 06:08 | 0.0843
2023-12-18 06:09 | 0.0839
2023-12-18 06:10 | 0.0838
2023-12-18 06:11 | 0.0839
2023-12-18 06:12 | 0.0839
2023-12-18 06:13 | 0.0841
2023-12-18 06:14 | 0.0843
2023-12-18 06:15 | 0.0843
2023-12-18 06:16 | 0.0846
2023-12-18 06:17 | 0.0845
2023-12-18 06:18 | 0.0847
2023-12-18 06:19 | 0.0846
2023-12-18 06:20 | 0.0849
2023-12-18 06:21 | 0.0849
2023-12-18 06:22 | 0.0845
2023-12-18 06:23 | 0.0847
2023-12-18 06:24 | 0.0848
2023-12-18 06:25 | 0.085
2023-12-18 06:26 | 0.0847
2023-12-18 06:27 | 0.0847
2023-12-18 06:28 | 0.0852
2023-12-18 06:29 | 0.0847
2023-12-18 06:30 | 0.0848
2023-12-18 06:31 | 0.0847
2023-12-18 06:32 | 0.0847
2023-12-18 06:33 | 0.0847
2023-12-18 06:34 | 0.0845
2023-12-18 06:35 | 0.0847
2023-12-18 06:36 | 0.0847
2023-12-18 06:37 | 0.0845
2023-12-18 06:38 | 0.0846
2023-12-18 06:39 | 0.0843
2023-12-18 06:40 | 0.0846
2023-12-18 06:41 | 0.0845
2023-12-18 06:42 | 0.0847
2023-12-18 06:43 | 0.0849
2023-12-18 06:44 | 0.0851
2023-12-18 06:45 | 0.0853
2023-12-18 06:46 | 0.0848
2023-12-18 06:47 | 0.0849
2023-12-18 06:48 | 0.0851
2023-12-18 06:49 | 0.0842
2023-12-18 06:50 | 0.0789
2023-12-18 06:51 | 0
2023-12-18 06:52 | 0
2023-12-18 06:53 | 0
2023-12-18 06:54 | 0
2023-12-18 06:55 | 0
2023-12-18 06:56 | 0.0103
2023-12-18 06:57 | 0.0835
2023-12-18 06:58 | 0.0837
2023-12-18 06:59 | 0.0839
2023-12-18 07:00 | 0.0835
2023-12-18 07:01 | 0.084
2023-12-18 07:02 | 0.0829
2023-12-18 07:03 | 0.083
2023-12-18 07:04 | 0.0835
2023-12-18 07:05 | 0.0829
2023-12-18 07:06 | 0.0836
2023-12-18 07:07 | 0.0836
2023-12-18 07:08 | 0.0839
2023-12-18 07:09 | 0.0833
2023-12-18 07:10 | 0.0834
2023-12-18 07:11 | 0.0837
2023-12-18 07:12 | 0.0834
2023-12-18 07:13 | 0.0835
2023-12-18 07:14 | 0.0838
2023-12-18 07:15 | 0.0837
2023-12-18 07:16 | 0.0841
2023-12-18 07:17 | 0.0839
2023-12-18 07:18 | 0.0839
2023-12-18 07:19 | 0.084
2023-12-18 07:20 | 0.084
2023-12-18 07:21 | 0.0841
2023-12-18 07:22 | 0.0841
2023-12-18 07:23 | 0.084
2023-12-18 07:24 | 0.0839
2023-12-18 07:25 | 0.084
2023-12-18 07:26 | 0.0841
2023-12-18 07:27 | 0.0842
2023-12-18 07:28 | 0.0839
2023-12-18 07:29 | 0.0839
2023-12-18 07:30 | 0.0843
2023-12-18 07:31 | 0.0837
2023-12-18 07:32 | 0.084
2023-12-18 07:33 | 0.0836
2023-12-18 07:34 | 0.0834
2023-12-18 07:35 | 0.0836
2023-12-18 07:36 | 0.0835
2023-12-18 07:37 | 0.0835
2023-12-18 07:38 | 0.0836
2023-12-18 07:39 | 0.0834
2023-12-18 07:40 | 0.0838
2023-12-18 07:41 | 0.0837
2023-12-18 07:42 | 0.084
2023-12-18 07:43 | 0.0835
2023-12-18 07:44 | 0.0833
2023-12-18 07:45 | 0.0837
2023-12-18 07:46 | 0.0834
2023-12-18 07:47 | 0.0834
2023-12-18 07:48 | 0.0835
2023-12-18 07:49 | 0.0835
2023-12-18 07:50 | 0.0832
2023-12-18 07:51 | 0.0158
2023-12-18 07:52 | 0
2023-12-18 07:53 | 0
2023-12-18 07:54 | 0
2023-12-18 07:55 | 0
2023-12-18 07:56 | 0
2023-12-18 07:57 | 0.0726
2023-12-18 07:58 | 0.0824
2023-12-18 07:59 | 0.0833
2023-12-18 08:00 | 0.0832
2023-12-18 08:01 | 0.0832
2023-12-18 08:02 | 0.0827
2023-12-18 08:03 | 0.0831
2023-12-18 08:04 | 0.083
2023-12-18 08:05 | 0.0829
2023-12-18 08:06 | 0.0829
2023-12-18 08:07 | 0.0832
2023-12-18 08:08 | 0.0835
2023-12-18 08:09 | 0.0832
2023-12-18 08:10 | 0.0836
2023-12-18 08:11 | 0.0834
2023-12-18 08:12 | 0.083
2023-12-18 08:13 | 0.0835
2023-12-18 08:14 | 0.0841
2023-12-18 08:15 | 0.0828
2023-12-18 08:16 | 0.083
2023-12-18 08:17 | 0.0836
2023-12-18 08:18 | 0.0834
2023-12-18 08:19 | 0.0835
2023-12-18 08:20 | 0.0836
2023-12-18 08:21 | 0.0835
2023-12-18 08:22 | 0.0835
2023-12-18 08:23 | 0.0837
2023-12-18 08:24 | 0.0837
2023-12-18 08:25 | 0.0839
2023-12-18 08:26 | 0.0839
2023-12-18 08:27 | 0.0839
2023-12-18 08:28 | 0.084
2023-12-18 08:29 | 0.0832
2023-12-18 08:30 | 0.0835
2023-12-18 08:31 | 0.0835
2023-12-18 08:32 | 0.0834
2023-12-18 08:33 | 0.0833
2023-12-18 08:34 | 0.0832
2023-12-18 08:35 | 0.0835
2023-12-18 08:36 | 0.0839
2023-12-18 08:37 | 0.0835
2023-12-18 08:38 | 0.0832
2023-12-18 08:39 | 0.0834
2023-12-18 08:40 | 0.0834
2023-12-18 08:41 | 0.0834
2023-12-18 08:42 | 0.0834
2023-12-18 08:43 | 0.0835
2023-12-18 08:44 | 0.0837
2023-12-18 08:45 | 0.0839
2023-12-18 08:46 | 0.0836
2023-12-18 08:47 | 0.083
2023-12-18 08:48 | 0.0835
2023-12-18 08:49 | 0.0835
2023-12-18 08:50 | 0.0825
2023-12-18 08:51 | 0.0407
2023-12-18 08:52 | 0
2023-12-18 08:53 | 0
2023-12-18 08:54 | 0
2023-12-18 08:55 | 0
2023-12-18 08:56 | 0
2023-12-18 08:57 | 0.0484
2023-12-18 08:58 | 0.0824
2023-12-18 08:59 | 0.083
2023-12-18 09:00 | 0.0832
2023-12-18 09:01 | 0.0829
2023-12-18 09:02 | 0.0825
2023-12-18 09:03 | 0.0826
2023-12-18 09:04 | 0.083
2023-12-18 09:05 | 0.0827
2023-12-18 09:06 | 0.083
2023-12-18 09:07 | 0.0831
2023-12-18 09:08 | 0.0827
2023-12-18 09:09 | 0.0827
2023-12-18 09:10 | 0.0826
2023-12-18 09:11 | 0.0825
2023-12-18 09:12 | 0.0825
2023-12-18 09:13 | 0.0826
2023-12-18 09:14 | 0.0827
2023-12-18 09:15 | 0.0831
2023-12-18 09:16 | 0.083
2023-12-18 09:17 | 0.0825
2023-12-18 09:18 | 0.0826
2023-12-18 09:19 | 0.0826
2023-12-18 09:20 | 0.0826
2023-12-18 09:21 | 0.0828
2023-12-18 09:22 | 0.0825
2023-12-18 09:23 | 0.0831
2023-12-18 09:24 | 0.0829
2023-12-18 09:25 | 0.0826
2023-12-18 09:26 | 0.083
2023-12-18 09:27 | 0.0826
2023-12-18 09:28 | 0.0828
2023-12-18 09:29 | 0.083
2023-12-18 09:30 | 0.0829
2023-12-18 09:31 | 0.0828
2023-12-18 09:32 | 0.0824
2023-12-18 09:33 | 0.0826
2023-12-18 09:34 | 0.0828
2023-12-18 09:35 | 0.0825
2023-12-18 09:36 | 0.0826
2023-12-18 09:37 | 0.0827
2023-12-18 09:38 | 0.0826
2023-12-18 09:39 | 0.0828
2023-12-18 09:40 | 0.0826
2023-12-18 09:41 | 0.0829
2023-12-18 09:42 | 0.0825
2023-12-18 09:43 | 0.0829
2023-12-18 09:44 | 0.0829
2023-12-18 09:45 | 0.0831
2023-12-18 09:46 | 0.083
2023-12-18 09:47 | 0.0826
2023-12-18 09:48 | 0.0832
2023-12-18 09:49 | 0.0831
2023-12-18 09:50 | 0.0829
2023-12-18 09:51 | 0.0621
2023-12-18 09:52 | 0
2023-12-18 09:53 | 0
2023-12-18 09:54 | 0
2023-12-18 09:55 | 0
2023-12-18 09:56 | 0
2023-12-18 09:57 | 0.0247
2023-12-18 09:58 | 0.0832
2023-12-18 09:59 | 0.0835
2023-12-18 10:00 | 0.0831
2023-12-18 10:01 | 0.0831
2023-12-18 10:02 | 0.0833
2023-12-18 10:03 | 0.0832
2023-12-18 10:04 | 0.0839
2023-12-18 10:05 | 0.0841
2023-12-18 10:06 | 0.0842
2023-12-18 10:07 | 0.0842
2023-12-18 10:08 | 0.084
2023-12-18 10:09 | 0.0846
2023-12-18 10:10 | 0.0841
2023-12-18 10:11 | 0.0836
2023-12-18 10:12 | 0.0837
2023-12-18 10:13 | 0.084
2023-12-18 10:14 | 0.0834
2023-12-18 10:15 | 0.0834
2023-12-18 10:16 | 0.0837
2023-12-18 10:17 | 0.0839
2023-12-18 10:18 | 0.0838
2023-12-18 10:19 | 0.0835
2023-12-18 10:20 | 0.0838
2023-12-18 10:21 | 0.0837
2023-12-18 10:22 | 0.0836
2023-12-18 10:23 | 0.0839
2023-12-18 10:24 | 0.084
2023-12-18 10:25 | 0.084
2023-12-18 10:26 | 0.0837
2023-12-18 10:27 | 0.0839
2023-12-18 10:28 | 0.0838
2023-12-18 10:29 | 0.0836
2023-12-18 10:30 | 0.0838
2023-12-18 10:31 | 0.0836
2023-12-18 10:32 | 0.0838
2023-12-18 10:33 | 0.0834
2023-12-18 10:34 | 0.0834
2023-12-18 10:35 | 0.0833
2023-12-18 10:36 | 0.0839
2023-12-18 10:37 | 0.0837
2023-12-18 10:38 | 0.084
2023-12-18 10:39 | 0.0837
2023-12-18 10:40 | 0.0839
2023-12-18 10:41 | 0.0838
2023-12-18 10:42 | 0.0839
2023-12-18 10:43 | 0.084
2023-12-18 10:44 | 0.0839
2023-12-18 10:45 | 0.0839
2023-12-18 10:46 | 0.0841
2023-12-18 10:47 | 0.0843
2023-12-18 10:48 | 0.0838
2023-12-18 10:49 | 0.0839
2023-12-18 10:50 | 0.0839
2023-12-18 10:51 | 0.0838
2023-12-18 10:52 | 0.0033
2023-12-18 10:53 | 0
2023-12-18 10:54 | 0
2023-12-18 10:55 | 0
2023-12-18 10:56 | 0
2023-12-18 10:57 | 0
2023-12-18 10:58 | 0.0838
2023-12-18 10:59 | 0.0837
2023-12-18 11:00 | 0.0835
2023-12-18 11:01 | 0.0839
2023-12-18 11:02 | 0.0839
2023-12-18 11:03 | 0.0838
2023-12-18 11:04 | 0.0839
2023-12-18 11:05 | 0.0832
2023-12-18 11:06 | 0.0839
2023-12-18 11:07 | 0.0839
2023-12-18 11:08 | 0.0831
2023-12-18 11:09 | 0.083
2023-12-18 11:10 | 0.0828
2023-12-18 11:11 | 0.0832
2023-12-18 11:12 | 0.0828
2023-12-18 11:13 | 0.0833
2023-12-18 11:14 | 0.0837
2023-12-18 11:15 | 0.0835
2023-12-18 11:16 | 0.083
2023-12-18 11:17 | 0.0834
2023-12-18 11:18 | 0.083
2023-12-18 11:19 | 0.0828
2023-12-18 11:20 | 0.0826
2023-12-18 11:21 | 0.0831
2023-12-18 11:22 | 0.0831
2023-12-18 11:23 | 0.0833
2023-12-18 11:24 | 0.0836
2023-12-18 11:25 | 0.0831
2023-12-18 11:26 | 0.0833
2023-12-18 11:27 | 0.083
2023-12-18 11:28 | 0.0832
2023-12-18 11:29 | 0.0832
2023-12-18 11:30 | 0.0832
2023-12-18 11:31 | 0.0834
2023-12-18 11:32 | 0.0827
2023-12-18 11:33 | 0.0832
2023-12-18 11:34 | 0.0832
2023-12-18 11:35 | 0.0833
2023-12-18 11:36 | 0.0832
2023-12-18 11:37 | 0.0835
2023-12-18 11:38 | 0.0836
2023-12-18 11:39 | 0.0834
2023-12-18 11:40 | 0.0835
2023-12-18 11:41 | 0.0836
2023-12-18 11:42 | 0.0834
2023-12-18 11:43 | 0.0833
2023-12-18 11:44 | 0.0834
2023-12-18 11:45 | 0.0832
2023-12-18 11:46 | 0.0829
2023-12-18 11:47 | 0.0828
2023-12-18 11:48 | 0.0823
2023-12-18 11:49 | 0.0825
2023-12-18 11:50 | 0.0827
2023-12-18 11:51 | 0.0821
2023-12-18 11:52 | 0.0273
2023-12-18 11:53 | 0
2023-12-18 11:54 | 0
2023-12-18 11:55 | 0
2023-12-18 11:56 | 0
2023-12-18 11:57 | 0
2023-12-18 11:58 | 0.0591
2023-12-18 11:59 | 0.0826
2023-12-18 12:00 | 0.0826
2023-12-18 12:01 | 0.0828
2023-12-18 12:02 | 0.0827
2023-12-18 12:03 | 0.083
2023-12-18 12:04 | 0.0831
2023-12-18 12:05 | 0.0831
2023-12-18 12:06 | 0.0828
2023-12-18 12:07 | 0.0826
2023-12-18 12:08 | 0.0826
2023-12-18 12:09 | 0.0826
2023-12-18 12:10 | 0.0829
2023-12-18 12:11 | 0.0828
2023-12-18 12:12 | 0.0831
2023-12-18 12:13 | 0.0831
2023-12-18 12:14 | 0.0823
2023-12-18 12:15 | 0.0825
2023-12-18 12:16 | 0.0825
2023-12-18 12:17 | 0.0824
2023-12-18 12:18 | 0.0826
2023-12-18 12:19 | 0.0828
2023-12-18 12:20 | 0.0826
2023-12-18 12:21 | 0.0829
2023-12-18 12:22 | 0.0831
2023-12-18 12:23 | 0.083
2023-12-18 12:24 | 0.0829
2023-12-18 12:25 | 0.0832
2023-12-18 12:26 | 0.0832
2023-12-18 12:27 | 0.0828
2023-12-18 12:28 | 0.0829
2023-12-18 12:29 | 0.083
2023-12-18 12:30 | 0.0832
2023-12-18 12:31 | 0.0829
2023-12-18 12:32 | 0.0828
2023-12-18 12:33 | 0.0826
2023-12-18 12:34 | 0.0828
2023-12-18 12:35 | 0.0827
2023-12-18 12:36 | 0.0828
2023-12-18 12:37 | 0.0827
2023-12-18 12:38 | 0.0829
2023-12-18 12:39 | 0.0831
2023-12-18 12:40 | 0.0831
2023-12-18 12:41 | 0.0829
2023-12-18 12:42 | 0.0831
2023-12-18 12:43 | 0.0829
2023-12-18 12:44 | 0.0827
2023-12-18 12:45 | 0.0829
2023-12-18 12:46 | 0.0832
2023-12-18 12:47 | 0.0827
2023-12-18 12:48 | 0.0831
2023-12-18 12:49 | 0.083
2023-12-18 12:50 | 0.0832
2023-12-18 12:51 | 0.0828
2023-12-18 12:52 | 0.0503
2023-12-18 12:53 | 0
2023-12-18 12:54 | 0
2023-12-18 12:55 | 0
2023-12-18 12:56 | 0
2023-12-18 12:57 | 0
2023-12-18 12:58 | 0.0363
2023-12-18 12:59 | 0.0828
2023-12-18 13:00 | 0.0829
2023-12-18 13:01 | 0.0831
2023-12-18 13:02 | 0.0831
2023-12-18 13:03 | 0.0835
2023-12-18 13:04 | 0.0831
2023-12-18 13:05 | 0.0832
2023-12-18 13:06 | 0.0833
2023-12-18 13:07 | 0.0833
2023-12-18 13:08 | 0.0834
2023-12-18 13:09 | 0.0834
2023-12-18 13:10 | 0.0833
2023-12-18 13:11 | 0.0835
2023-12-18 13:12 | 0.0836
2023-12-18 13:13 | 0.0833
2023-12-18 13:14 | 0.0832
2023-12-18 13:15 | 0.0833
2023-12-18 13:16 | 0.0834
2023-12-18 13:17 | 0.0834
2023-12-18 13:18 | 0.0833
2023-12-18 13:19 | 0.0834
2023-12-18 13:20 | 0.0833
2023-12-18 13:21 | 0.0835
2023-12-18 13:22 | 0.0833
2023-12-18 13:23 | 0.0832
2023-12-18 13:24 | 0.0832
2023-12-18 13:25 | 0.0828
2023-12-18 13:26 | 0.0829
2023-12-18 13:27 | 0.0832
2023-12-18 13:28 | 0.0834
2023-12-18 13:29 | 0.0831
2023-12-18 13:30 | 0.0832
2023-12-18 13:31 | 0.0832
2023-12-18 13:32 | 0.0829
2023-12-18 13:33 | 0.083
2023-12-18 13:34 | 0.0831
2023-12-18 13:35 | 0.0832
2023-12-18 13:36 | 0.0833
2023-12-18 13:37 | 0.0831
2023-12-18 13:38 | 0.0829
2023-12-18 13:39 | 0.0828
2023-12-18 13:40 | 0.0832
2023-12-18 13:41 | 0.0829
2023-12-18 13:42 | 0.0829
2023-12-18 13:43 | 0.0829
2023-12-18 13:44 | 0.0831
2023-12-18 13:45 | 0.083
2023-12-18 13:46 | 0.0831
2023-12-18 13:47 | 0.0832
2023-12-18 13:48 | 0.0832
2023-12-18 13:49 | 0.0829
2023-12-18 13:50 | 0.083
2023-12-18 13:51 | 0.0831
2023-12-18 13:52 | 0.0746
2023-12-18 13:53 | 0
2023-12-18 13:54 | 0
2023-12-18 13:55 | 0
2023-12-18 13:56 | 0
2023-12-18 13:57 | 0
2023-12-18 13:58 | 0.0121
2023-12-18 13:59 | 0.083
2023-12-18 14:00 | 0.0831
2023-12-18 14:01 | 0.083
2023-12-18 14:02 | 0.0832
2023-12-18 14:03 | 0.0831
2023-12-18 14:04 | 0.0831
2023-12-18 14:05 | 0.0833
2023-12-18 14:06 | 0.0823
2023-12-18 14:07 | 0.0821
2023-12-18 14:08 | 0.0826
2023-12-18 14:09 | 0.0832
2023-12-18 14:10 | 0.0831
2023-12-18 14:11 | 0.0832
2023-12-18 14:12 | 0.0833
2023-12-18 14:13 | 0.0834
2023-12-18 14:14 | 0.0833
2023-12-18 14:15 | 0.0832
2023-12-18 14:16 | 0.0833
2023-12-18 14:17 | 0.0834
2023-12-18 14:18 | 0.0831
2023-12-18 14:19 | 0.083
2023-12-18 14:20 | 0.0829
2023-12-18 14:21 | 0.0829
2023-12-18 14:22 | 0.0828
2023-12-18 14:23 | 0.0825
2023-12-18 14:24 | 0.0818
2023-12-18 14:25 | 0.082
2023-12-18 14:26 | 0.0815
2023-12-18 14:27 | 0.0822
2023-12-18 14:28 | 0.0823
2023-12-18 14:29 | 0.0817
2023-12-18 14:30 | 0.0821
2023-12-18 14:31 | 0.083
2023-12-18 14:32 | 0.083
2023-12-18 14:33 | 0.0831
2023-12-18 14:34 | 0.0829
2023-12-18 14:35 | 0.083
2023-12-18 14:36 | 0.0829
2023-12-18 14:37 | 0.083
2023-12-18 14:38 | 0.083
2023-12-18 14:39 | 0.083
2023-12-18 14:40 | 0.0828
2023-12-18 14:41 | 0.0832
2023-12-18 14:42 | 0.0828
2023-12-18 14:43 | 0.0829
2023-12-18 14:44 | 0.0831
2023-12-18 14:45 | 0.0829
2023-12-18 14:46 | 0.0829
2023-12-18 14:47 | 0.0827
2023-12-18 14:48 | 0.0829
2023-12-18 14:49 | 0.0826
2023-12-18 14:50 | 0.0827
2023-12-18 14:51 | 0.0827
2023-12-18 14:52 | 0.0824
2023-12-18 14:53 | 0.0179
2023-12-18 14:54 | 0
2023-12-18 14:55 | 0
2023-12-18 14:56 | 0
2023-12-18 14:57 | 0
2023-12-18 14:58 | 0
2023-12-18 14:59 | 0.0677
2023-12-18 15:00 | 0.0824
2023-12-18 15:01 | 0.0824
2023-12-18 15:02 | 0.0826
2023-12-18 15:03 | 0.0824
2023-12-18 15:04 | 0.0826
2023-12-18 15:05 | 0.0824
2023-12-18 15:06 | 0.0824
2023-12-18 15:07 | 0.0825
2023-12-18 15:08 | 0.0825
2023-12-18 15:09 | 0.0825
2023-12-18 15:10 | 0.0825
2023-12-18 15:11 | 0.0827
2023-12-18 15:12 | 0.0825
2023-12-18 15:13 | 0.0825
2023-12-18 15:14 | 0.0823
2023-12-18 15:15 | 0.0826
2023-12-18 15:16 | 0.0827
2023-12-18 15:17 | 0.0825
2023-12-18 15:18 | 0.0826
2023-12-18 15:19 | 0.0824
2023-12-18 15:20 | 0.0825
2023-12-18 15:21 | 0.0825
2023-12-18 15:22 | 0.0826
2023-12-18 15:23 | 0.0827
2023-12-18 15:24 | 0.0823
2023-12-18 15:25 | 0.0826
2023-12-18 15:26 | 0.0823
2023-12-18 15:27 | 0.0826
2023-12-18 15:28 | 0.0824
2023-12-18 15:29 | 0.0824
2023-12-18 15:30 | 0.0825
2023-12-18 15:31 | 0.0825
2023-12-18 15:32 | 0.0825
2023-12-18 15:33 | 0.0825
2023-12-18 15:34 | 0.0826
2023-12-18 15:35 | 0.0826
2023-12-18 15:36 | 0.0822
2023-12-18 15:37 | 0.0823
2023-12-18 15:38 | 0.0825
2023-12-18 15:39 | 0.0824
2023-12-18 15:40 | 0.0823
2023-12-18 15:41 | 0.0824
2023-12-18 15:42 | 0.0818
2023-12-18 15:43 | 0.0823
2023-12-18 15:44 | 0.0826
2023-12-18 15:45 | 0.0821
2023-12-18 15:46 | 0.0822
2023-12-18 15:47 | 0.0822
2023-12-18 15:48 | 0.0824
2023-12-18 15:49 | 0.0821
2023-12-18 15:50 | 0.082
2023-12-18 15:51 | 0.0821
2023-12-18 15:52 | 0.0823
2023-12-18 15:53 | 0.0452
2023-12-18 15:54 | 0
2023-12-18 15:55 | 0
2023-12-18 15:56 | 0
2023-12-18 15:57 | 0
2023-12-18 15:58 | 0
2023-12-18 15:59 | 0.0401
2023-12-18 16:00 | 0.0815
2023-12-18 16:01 | 0.0818
2023-12-18 16:02 | 0.0817
2023-12-18 16:03 | 0.082
2023-12-18 16:04 | 0.082
2023-12-18 16:05 | 0.0821
2023-12-18 16:06 | 0.0819
2023-12-18 16:07 | 0.0816
2023-12-18 16:08 | 0.0818
2023-12-18 16:09 | 0.0815
2023-12-18 16:10 | 0.0816
2023-12-18 16:11 | 0.0818
2023-12-18 16:12 | 0.0815
2023-12-18 16:13 | 0.0819
2023-12-18 16:14 | 0.0819
2023-12-18 16:15 | 0.0815
2023-12-18 16:16 | 0.0819
2023-12-18 16:17 | 0.0819
2023-12-18 16:18 | 0.0819
2023-12-18 16:19 | 0.0818
2023-12-18 16:20 | 0.082
2023-12-18 16:21 | 0.0819
2023-12-18 16:22 | 0.0817
2023-12-18 16:23 | 0.0819
2023-12-18 16:24 | 0.0819
2023-12-18 16:25 | 0.0819
2023-12-18 16:26 | 0.0818
2023-12-18 16:27 | 0.0818
2023-12-18 16:28 | 0.0821
2023-12-18 16:29 | 0.0822
2023-12-18 16:30 | 0.0818
2023-12-18 16:31 | 0.0817
2023-12-18 16:32 | 0.0817
2023-12-18 16:33 | 0.0815
2023-12-18 16:34 | 0.0819
2023-12-18 16:35 | 0.0817
2023-12-18 16:36 | 0.082
2023-12-18 16:37 | 0.0818
2023-12-18 16:38 | 0.0817
2023-12-18 16:39 | 0.0816
2023-12-18 16:40 | 0.0816
2023-12-18 16:41 | 0.0816
2023-12-18 16:42 | 0.0819
2023-12-18 16:43 | 0.0818
2023-12-18 16:44 | 0.0819
2023-12-18 16:45 | 0.0819
2023-12-18 16:46 | 0.0818
2023-12-18 16:47 | 0.0818
2023-12-18 16:48 | 0.0818
2023-12-18 16:49 | 0.0817
2023-12-18 16:50 | 0.082
2023-12-18 16:51 | 0.0818
2023-12-18 16:52 | 0.0815
2023-12-18 16:53 | 0.0718
2023-12-18 16:54 | 0
2023-12-18 16:55 | 0
2023-12-18 16:56 | 0
2023-12-18 16:57 | 0
2023-12-18 16:58 | 0
2023-12-18 16:59 | 0.0125
2023-12-18 17:00 | 0.0811
2023-12-18 17:01 | 0.0814
2023-12-18 17:02 | 0.0812
2023-12-18 17:03 | 0.0809
2023-12-18 17:04 | 0.0809
2023-12-18 17:05 | 0.0813
2023-12-18 17:06 | 0.0809
2023-12-18 17:07 | 0.0809
2023-12-18 17:08 | 0.081
2023-12-18 17:09 | 0.0812
2023-12-18 17:10 | 0.081
2023-12-18 17:11 | 0.0815
2023-12-18 17:12 | 0.0809
2023-12-18 17:13 | 0.0805
2023-12-18 17:14 | 0.0803
2023-12-18 17:15 | 0.0811
2023-12-18 17:16 | 0.0805
2023-12-18 17:17 | 0.0801
2023-12-18 17:18 | 0.0809
2023-12-18 17:19 | 0.0804
2023-12-18 17:20 | 0.0806
2023-12-18 17:21 | 0.0811
2023-12-18 17:22 | 0.0818
2023-12-18 17:23 | 0.0806
2023-12-18 17:24 | 0.0812
2023-12-18 17:25 | 0.0812
2023-12-18 17:26 | 0.0813
2023-12-18 17:27 | 0.0813
2023-12-18 17:28 | 0.0809
2023-12-18 17:29 | 0.0817
2023-12-18 17:30 | 0.0811
2023-12-18 17:31 | 0.0816
2023-12-18 17:32 | 0.0814
2023-12-18 17:33 | 0.0817
2023-12-18 17:34 | 0.0813
2023-12-18 17:35 | 0.0816
2023-12-18 17:36 | 0.0815
2023-12-18 17:37 | 0.0816
2023-12-18 17:38 | 0.0818
2023-12-18 17:39 | 0.0818
2023-12-18 17:40 | 0.0821
2023-12-18 17:41 | 0.0817
2023-12-18 17:42 | 0.0819
2023-12-18 17:43 | 0.0811
2023-12-18 17:44 | 0.0815
2023-12-18 17:45 | 0.082
2023-12-18 17:46 | 0.0816
2023-12-18 17:47 | 0.0814
2023-12-18 17:48 | 0.082
2023-12-18 17:49 | 0.0817
2023-12-18 17:50 | 0.0816
2023-12-18 17:51 | 0.0813
2023-12-18 17:52 | 0.0823
2023-12-18 17:53 | 0.0819
2023-12-18 17:54 | 0.0202
2023-12-18 17:55 | 0
2023-12-18 17:56 | 0
2023-12-18 17:57 | 0
2023-12-18 17:58 | 0
2023-12-18 17:59 | 0
2023-12-18 18:00 | 0.064
2023-12-18 18:01 | 0.081
2023-12-18 18:02 | 0.0817
2023-12-18 18:03 | 0.0818
2023-12-18 18:04 | 0.0817
2023-12-18 18:05 | 0.0818
2023-12-18 18:06 | 0.0821
2023-12-18 18:07 | 0.0817
2023-12-18 18:08 | 0.0817
2023-12-18 18:09 | 0.0821
2023-12-18 18:10 | 0.0819
2023-12-18 18:11 | 0.0817
2023-12-18 18:12 | 0.0821
2023-12-18 18:13 | 0.0819
2023-12-18 18:14 | 0.0819
2023-12-18 18:15 | 0.082
2023-12-18 18:16 | 0.0823
2023-12-18 18:17 | 0.0823
2023-12-18 18:18 | 0.0824
2023-12-18 18:19 | 0.0824
2023-12-18 18:20 | 0.0816
2023-12-18 18:21 | 0.0819
2023-12-18 18:22 | 0.083
2023-12-18 18:23 | 0.0829
2023-12-18 18:24 | 0.0831
2023-12-18 18:25 | 0.0826
2023-12-18 18:26 | 0.0824
2023-12-18 18:27 | 0.0829
2023-12-18 18:28 | 0.0827
2023-12-18 18:29 | 0.082
2023-12-18 18:30 | 0.0816
2023-12-18 18:31 | 0.081
2023-12-18 18:32 | 0.0815
2023-12-18 18:33 | 0.0822
2023-12-18 18:34 | 0.0817
2023-12-18 18:35 | 0.0823
2023-12-18 18:36 | 0.082
2023-12-18 18:37 | 0.0824
2023-12-18 18:38 | 0.0823
2023-12-18 18:39 | 0.0821
2023-12-18 18:40 | 0.0813
2023-12-18 18:41 | 0.0824
2023-12-18 18:42 | 0.0823
2023-12-18 18:43 | 0.0828
2023-12-18 18:44 | 0.082
2023-12-18 18:45 | 0.0824
2023-12-18 18:46 | 0.0817
2023-12-18 18:47 | 0.0824
2023-12-18 18:48 | 0.0822
2023-12-18 18:49 | 0.0822
2023-12-18 18:50 | 0.0826
2023-12-18 18:51 | 0.0821
2023-12-18 18:52 | 0.0824
2023-12-18 18:53 | 0.0822
2023-12-18 18:54 | 0.0561
2023-12-18 18:55 | 0
2023-12-18 18:56 | 0
2023-12-18 18:57 | 0
2023-12-18 18:58 | 0
2023-12-18 18:59 | 0
2023-12-18 19:00 | 0.0279
2023-12-18 19:01 | 0.0816
2023-12-18 19:02 | 0.0812
2023-12-18 19:03 | 0.0819
2023-12-18 19:04 | 0.0827
2023-12-18 19:05 | 0.0826
2023-12-18 19:06 | 0.0811
2023-12-18 19:07 | 0.0823
2023-12-18 19:08 | 0.0814
2023-12-18 19:09 | 0.0825
2023-12-18 19:10 | 0.082
2023-12-18 19:11 | 0.0822
2023-12-18 19:12 | 0.0827
2023-12-18 19:13 | 0.0817
2023-12-18 19:14 | 0.0821
2023-12-18 19:15 | 0.0827
2023-12-18 19:16 | 0.0825
2023-12-18 19:17 | 0.0826
2023-12-18 19:18 | 0.0824
2023-12-18 19:19 | 0.0825
2023-12-18 19:20 | 0.0825
2023-12-18 19:21 | 0.0819
2023-12-18 19:22 | 0.0817
2023-12-18 19:23 | 0.0825
2023-12-18 19:24 | 0.0819
2023-12-18 19:25 | 0.0827
2023-12-18 19:26 | 0.0828
2023-12-18 19:27 | 0.0826
2023-12-18 19:28 | 0.0821
2023-12-18 19:29 | 0.0819
2023-12-18 19:30 | 0.0819
2023-12-18 19:31 | 0.0816
2023-12-18 19:32 | 0.0828
2023-12-18 19:33 | 0.082
2023-12-18 19:34 | 0.082
2023-12-18 19:35 | 0.0822
2023-12-18 19:36 | 0.0827
2023-12-18 19:37 | 0.0826
2023-12-18 19:38 | 0.0831
2023-12-18 19:39 | 0.0825
2023-12-18 19:40 | 0.0822
2023-12-18 19:41 | 0.0819
2023-12-18 19:42 | 0.0823
2023-12-18 19:43 | 0.0822
2023-12-18 19:44 | 0.0818
2023-12-18 19:45 | 0.0825
2023-12-18 19:46 | 0.0828
2023-12-18 19:47 | 0.083
2023-12-18 19:48 | 0.0818
2023-12-18 19:49 | 0.0828
2023-12-18 19:50 | 0.0828
2023-12-18 19:51 | 0.0824
2023-12-18 19:52 | 0.0827
2023-12-18 19:53 | 0.0828
2023-12-18 19:54 | 0.0835
2023-12-18 19:55 | 0.0148
2023-12-18 19:56 | 0
2023-12-18 19:57 | 0
2023-12-18 19:58 | 0
2023-12-18 19:59 | 0
2023-12-18 20:00 | 0
2023-12-18 20:01 | 0.0698
2023-12-18 20:02 | 0.0828
2023-12-18 20:03 | 0.0829
2023-12-18 20:04 | 0.0831
2023-12-18 20:05 | 0.0834
2023-12-18 20:06 | 0.0821
2023-12-18 20:07 | 0.0827
2023-12-18 20:08 | 0.0832
2023-12-18 20:09 | 0.0832
2023-12-18 20:10 | 0.0828
2023-12-18 20:11 | 0.083
2023-12-18 20:12 | 0.0827
2023-12-18 20:13 | 0.0828
2023-12-18 20:14 | 0.0829
2023-12-18 20:15 | 0.0832
2023-12-18 20:16 | 0.0829
2023-12-18 20:17 | 0.0827
2023-12-18 20:18 | 0.083
2023-12-18 20:19 | 0.083
2023-12-18 20:20 | 0.0826
2023-12-18 20:21 | 0.0822
2023-12-18 20:22 | 0.0824
2023-12-18 20:23 | 0.0824
2023-12-18 20:24 | 0.0827
2023-12-18 20:25 | 0.083
2023-12-18 20:26 | 0.083
2023-12-18 20:27 | 0.0833
2023-12-18 20:28 | 0.0829
2023-12-18 20:29 | 0.0832
2023-12-18 20:30 | 0.0827
2023-12-18 20:31 | 0.0833
2023-12-18 20:32 | 0.0831
2023-12-18 20:33 | 0.0823
2023-12-18 20:34 | 0.0832
2023-12-18 20:35 | 0.0827
2023-12-18 20:36 | 0.0826
2023-12-18 20:37 | 0.0831
2023-12-18 20:38 | 0.0829
2023-12-18 20:39 | 0.0828
2023-12-18 20:40 | 0.0823
2023-12-18 20:41 | 0.0829
2023-12-18 20:42 | 0.0829
2023-12-18 20:43 | 0.083
2023-12-18 20:44 | 0.0836
2023-12-18 20:45 | 0.0837
2023-12-18 20:46 | 0.0835
2023-12-18 20:47 | 0.084
2023-12-18 20:48 | 0.0833
2023-12-18 20:49 | 0.0831
2023-12-18 20:50 | 0.0839
2023-12-18 20:51 | 0.0836
2023-12-18 20:52 | 0.0833
2023-12-18 20:53 | 0.0836
2023-12-18 20:54 | 0.0836
2023-12-18 20:55 | 0.0567
2023-12-18 20:56 | 0
2023-12-18 20:57 | 0
2023-12-18 20:58 | 0
2023-12-18 20:59 | 0
2023-12-18 21:00 | 0
2023-12-18 21:01 | 0.0291
2023-12-18 21:02 | 0.083
2023-12-18 21:03 | 0.0832
2023-12-18 21:04 | 0.0833
2023-12-18 21:05 | 0.0836
2023-12-18 21:06 | 0.0834
2023-12-18 21:07 | 0.0831
2023-12-18 21:08 | 0.0838
2023-12-18 21:09 | 0.084
2023-12-18 21:10 | 0.0841
2023-12-18 21:11 | 0.0836
2023-12-18 21:12 | 0.0838
2023-12-18 21:13 | 0.0839
2023-12-18 21:14 | 0.0837
2023-12-18 21:15 | 0.0839
2023-12-18 21:16 | 0.0845
2023-12-18 21:17 | 0.0841
2023-12-18 21:18 | 0.0841
2023-12-18 21:19 | 0.0843
2023-12-18 21:20 | 0.0842
2023-12-18 21:21 | 0.0839
2023-12-18 21:22 | 0.0844
2023-12-18 21:23 | 0.0844
2023-12-18 21:24 | 0.0842
2023-12-18 21:25 | 0.0841
2023-12-18 21:26 | 0.0845
2023-12-18 21:27 | 0.0841
2023-12-18 21:28 | 0.0836
2023-12-18 21:29 | 0.0844
2023-12-18 21:30 | 0.0849
2023-12-18 21:31 | 0.0848
2023-12-18 21:32 | 0.0847
2023-12-18 21:33 | 0.0846
2023-12-18 21:34 | 0.0847
2023-12-18 21:35 | 0.0846
2023-12-18 21:36 | 0.0848
2023-12-18 21:37 | 0.0844
2023-12-18 21:38 | 0.0843
2023-12-18 21:39 | 0.0845
2023-12-18 21:40 | 0.0843
2023-12-18 21:41 | 0.0844
2023-12-18 21:42 | 0.0846
2023-12-18 21:43 | 0.0849
2023-12-18 21:44 | 0.085
2023-12-18 21:45 | 0.0845
2023-12-18 21:46 | 0.0845
2023-12-18 21:47 | 0.0848
2023-12-18 21:48 | 0.0845
2023-12-18 21:49 | 0.0846
2023-12-18 21:50 | 0.0845
2023-12-18 21:51 | 0.0849
2023-12-18 21:52 | 0.0846
2023-12-18 21:53 | 0.0849
2023-12-18 21:54 | 0.0848
2023-12-18 21:55 | 0.085
2023-12-18 21:56 | 0.0109
2023-12-18 21:57 | 0
2023-12-18 21:58 | 0
2023-12-18 21:59 | 0
2023-12-18 22:00 | 0
2023-12-18 22:01 | 0
2023-12-18 22:02 | 0.0763
2023-12-18 22:03 | 0.0845
2023-12-18 22:04 | 0.0846
2023-12-18 22:05 | 0.0846
2023-12-18 22:06 | 0.0846
2023-12-18 22:07 | 0.0849
2023-12-18 22:08 | 0.085
2023-12-18 22:09 | 0.0849
2023-12-18 22:10 | 0.0851
2023-12-18 22:11 | 0.0849
2023-12-18 22:12 | 0.0851
2023-12-18 22:13 | 0.0849
2023-12-18 22:14 | 0.0852
2023-12-18 22:15 | 0.0848
2023-12-18 22:16 | 0.0853
2023-12-18 22:17 | 0.0852
2023-12-18 22:18 | 0.0853
2023-12-18 22:19 | 0.0853
2023-12-18 22:20 | 0.0855
2023-12-18 22:21 | 0.0853
2023-12-18 22:22 | 0.0852
2023-12-18 22:23 | 0.0854
2023-12-18 22:24 | 0.0852
2023-12-18 22:25 | 0.0853
2023-12-18 22:26 | 0.0851
2023-12-18 22:27 | 0.085
2023-12-18 22:28 | 0.0852
2023-12-18 22:29 | 0.0855
2023-12-18 22:30 | 0.0852
2023-12-18 22:31 | 0.0855
2023-12-18 22:32 | 0.0854
2023-12-18 22:33 | 0.0854
2023-12-18 22:34 | 0.0852
2023-12-18 22:35 | 0.0852
2023-12-18 22:36 | 0.0853
2023-12-18 22:37 | 0.0849
2023-12-18 22:38 | 0.0851
2023-12-18 22:39 | 0.0846
2023-12-18 22:40 | 0.085
2023-12-18 22:41 | 0.085
2023-12-18 22:42 | 0.0849
2023-12-18 22:43 | 0.0851
2023-12-18 22:44 | 0.0851
2023-12-18 22:45 | 0.0854
2023-12-18 22:46 | 0.0854
2023-12-18 22:47 | 0.0854
2023-12-18 22:48 | 0.0852
2023-12-18 22:49 | 0.0853
2023-12-18 22:50 | 0.0851
2023-12-18 22:51 | 0.0854
2023-12-18 22:52 | 0.0855
2023-12-18 22:53 | 0.0854
2023-12-18 22:54 | 0.0854
2023-12-18 22:55 | 0.0855
2023-12-18 22:56 | 0.0457
2023-12-18 22:57 | 0
2023-12-18 22:58 | 0
2023-12-18 22:59 | 0
2023-12-18 23:00 | 0
2023-12-18 23:01 | 0
2023-12-18 23:02 | 0.0425
2023-12-18 23:03 | 0.0848
2023-12-18 23:04 | 0.0853
2023-12-18 23:05 | 0.0853
2023-12-18 23:06 | 0.0854
2023-12-18 23:07 | 0.0855
2023-12-18 23:08 | 0.0855
2023-12-18 23:09 | 0.0854
2023-12-18 23:10 | 0.0853
2023-12-18 23:11 | 0.0857
2023-12-18 23:12 | 0.0857
2023-12-18 23:13 | 0.0857
2023-12-18 23:14 | 0.0856
2023-12-18 23:15 | 0.0856
2023-12-18 23:16 | 0.0856
2023-12-18 23:17 | 0.0855
2023-12-18 23:18 | 0.0858
2023-12-18 23:19 | 0.0858
2023-12-18 23:20 | 0.086
2023-12-18 23:21 | 0.086
2023-12-18 23:22 | 0.0858
2023-12-18 23:23 | 0.0859
2023-12-18 23:24 | 0.0859
2023-12-18 23:25 | 0.0859
2023-12-18 23:26 | 0.0856
2023-12-18 23:27 | 0.086
2023-12-18 23:28 | 0.0863
2023-12-18 23:29 | 0.086
2023-12-18 23:30 | 0.086
2023-12-18 23:31 | 0.0861
2023-12-18 23:32 | 0.0861
2023-12-18 23:33 | 0.0862
2023-12-18 23:34 | 0.0863
2023-12-18 23:35 | 0.0863
2023-12-18 23:36 | 0.086
2023-12-18 23:37 | 0.0861
2023-12-18 23:38 | 0.086
2023-12-18 23:39 | 0.086
2023-12-18 23:40 | 0.0862
2023-12-18 23:41 | 0.0862
2023-12-18 23:42 | 0.0862
2023-12-18 23:43 | 0.0863
2023-12-18 23:44 | 0.0863
2023-12-18 23:45 | 0.0861
2023-12-18 23:46 | 0.0856
2023-12-18 23:47 | 0.0859
2023-12-18 23:48 | 0.0859
2023-12-18 23:49 | 0.0857
2023-12-18 23:50 | 0.0859
2023-12-18 23:51 | 0.0856
2023-12-18 23:52 | 0.0859
2023-12-18 23:53 | 0.0856
2023-12-18 23:54 | 0.0858
2023-12-18 23:55 | 0.0854
2023-12-18 23:56 | 0.0763
2023-12-18 23:57 | 0
2023-12-18 23:58 | 0
2023-12-18 23:59 | 0
2023-12-19 | 0
2023-12-19 00:01 | 0
2023-12-19 00:02 | 0.0131
2023-12-19 00:03 | 0.0855
2023-12-19 00:04 | 0.0852
2023-12-19 00:05 | 0.0854
2023-12-19 00:06 | 0.0856
2023-12-19 00:07 | 0.0858
2023-12-19 00:08 | 0.0857
2023-12-19 00:09 | 0.0857
2023-12-19 00:10 | 0.0858
2023-12-19 00:11 | 0.0857
2023-12-19 00:12 | 0.0855
2023-12-19 00:13 | 0.0859
2023-12-19 00:14 | 0.0856
2023-12-19 00:15 | 0.0854
2023-12-19 00:16 | 0.0857
2023-12-19 00:17 | 0.0856
2023-12-19 00:18 | 0.0857
2023-12-19 00:19 | 0.0855
2023-12-19 00:20 | 0.0857
2023-12-19 00:21 | 0.0858
2023-12-19 00:22 | 0.0855
2023-12-19 00:23 | 0.0854
2023-12-19 00:24 | 0.0854
2023-12-19 00:25 | 0.0855
2023-12-19 00:26 | 0.0859
2023-12-19 00:27 | 0.0858
2023-12-19 00:28 | 0.0857
2023-12-19 00:29 | 0.0858
2023-12-19 00:30 | 0.0857
2023-12-19 00:31 | 0.0859
2023-12-19 00:32 | 0.0858
2023-12-19 00:33 | 0.0856
2023-12-19 00:34 | 0.0857
2023-12-19 00:35 | 0.0859
2023-12-19 00:36 | 0.0857
2023-12-19 00:37 | 0.0859
2023-12-19 00:38 | 0.0857
2023-12-19 00:39 | 0.0857
2023-12-19 00:40 | 0.0858
2023-12-19 00:41 | 0.0859
2023-12-19 00:42 | 0.0859
2023-12-19 00:43 | 0.0861
2023-12-19 00:44 | 0.0858
2023-12-19 00:45 | 0.086
2023-12-19 00:46 | 0.086
2023-12-19 00:47 | 0.086
2023-12-19 00:48 | 0.0859
2023-12-19 00:49 | 0.0854
2023-12-19 00:50 | 0.0859
2023-12-19 00:51 | 0.086
2023-12-19 00:52 | 0.086
2023-12-19 00:53 | 0.086
2023-12-19 00:54 | 0.0859
2023-12-19 00:55 | 0.0859
2023-12-19 00:56 | 0.0862
2023-12-19 00:57 | 0.0175
2023-12-19 00:58 | 0
2023-12-19 00:59 | 0
2023-12-19 01:00 | 0
2023-12-19 01:01 | 0
2023-12-19 01:02 | 0
2023-12-19 01:03 | 0.0722
2023-12-19 01:04 | 0.0857
2023-12-19 01:05 | 0.0858
2023-12-19 01:06 | 0.0857
2023-12-19 01:07 | 0.0855
2023-12-19 01:08 | 0.0853
2023-12-19 01:09 | 0.0857
2023-12-19 01:10 | 0.0858
2023-12-19 01:11 | 0.086
2023-12-19 01:12 | 0.0855
2023-12-19 01:13 | 0.0854
2023-12-19 01:14 | 0.0859
2023-12-19 01:15 | 0.0857
2023-12-19 01:16 | 0.0858
2023-12-19 01:17 | 0.0857
2023-12-19 01:18 | 0.0856
2023-12-19 01:19 | 0.0857
2023-12-19 01:20 | 0.0858
2023-12-19 01:21 | 0.0858
2023-12-19 01:22 | 0.0859
2023-12-19 01:23 | 0.0858
2023-12-19 01:24 | 0.0858
2023-12-19 01:25 | 0.0858
2023-12-19 01:26 | 0.0857
2023-12-19 01:27 | 0.0859
2023-12-19 01:28 | 0.0857
2023-12-19 01:29 | 0.0858
2023-12-19 01:30 | 0.0858
2023-12-19 01:31 | 0.0859
2023-12-19 01:32 | 0.086
2023-12-19 01:33 | 0.0858
2023-12-19 01:34 | 0.0857
2023-12-19 01:35 | 0.0858
2023-12-19 01:36 | 0.0858
2023-12-19 01:37 | 0.0859
2023-12-19 01:38 | 0.0857
2023-12-19 01:39 | 0.0858
2023-12-19 01:40 | 0.0856
2023-12-19 01:41 | 0.0857
2023-12-19 01:42 | 0.0857
2023-12-19 01:43 | 0.0857
2023-12-19 01:44 | 0.0855
2023-12-19 01:45 | 0.0857
2023-12-19 01:46 | 0.086
2023-12-19 01:47 | 0.0859
2023-12-19 01:48 | 0.0858
2023-12-19 01:49 | 0.0857
2023-12-19 01:50 | 0.086
2023-12-19 01:51 | 0.086
2023-12-19 01:52 | 0.0858
2023-12-19 01:53 | 0.0859
2023-12-19 01:54 | 0.0862
2023-12-19 01:55 | 0.0862
2023-12-19 01:56 | 0.0861
2023-12-19 01:57 | 0.0401
2023-12-19 01:58 | 0
2023-12-19 01:59 | 0
2023-12-19 02:00 | 0
2023-12-19 02:01 | 0
2023-12-19 02:02 | 0
2023-12-19 02:03 | 0.0509
2023-12-19 02:04 | 0.0855
2023-12-19 02:05 | 0.0857
2023-12-19 02:06 | 0.0857
2023-12-19 02:07 | 0.086
2023-12-19 02:08 | 0.086
2023-12-19 02:09 | 0.0859
2023-12-19 02:10 | 0.0859
2023-12-19 02:11 | 0.0859
2023-12-19 02:12 | 0.086
2023-12-19 02:13 | 0.086
2023-12-19 02:14 | 0.086
2023-12-19 02:15 | 0.0862
2023-12-19 02:16 | 0.0861
2023-12-19 02:17 | 0.0862
2023-12-19 02:18 | 0.0861
2023-12-19 02:19 | 0.086
2023-12-19 02:20 | 0.086
2023-12-19 02:21 | 0.0861
2023-12-19 02:22 | 0.0861
2023-12-19 02:23 | 0.0862
2023-12-19 02:24 | 0.0861
2023-12-19 02:25 | 0.086
2023-12-19 02:26 | 0.086
2023-12-19 02:27 | 0.086
2023-12-19 02:28 | 0.086
2023-12-19 02:29 | 0.086
2023-12-19 02:30 | 0.086
2023-12-19 02:31 | 0.0859
2023-12-19 02:32 | 0.0859
2023-12-19 02:33 | 0.0859
2023-12-19 02:34 | 0.086
2023-12-19 02:35 | 0.0862
2023-12-19 02:36 | 0.0863
2023-12-19 02:37 | 0.0861
2023-12-19 02:38 | 0.0861
2023-12-19 02:39 | 0.0861
2023-12-19 02:40 | 0.0863
2023-12-19 02:41 | 0.0861
2023-12-19 02:42 | 0.0862
2023-12-19 02:43 | 0.0862
2023-12-19 02:44 | 0.0861
2023-12-19 02:45 | 0.0861
2023-12-19 02:46 | 0.0861
2023-12-19 02:47 | 0.0862
2023-12-19 02:48 | 0.0864
2023-12-19 02:49 | 0.0863
2023-12-19 02:50 | 0.0864
2023-12-19 02:51 | 0.0862
2023-12-19 02:52 | 0.0861
2023-12-19 02:53 | 0.0862
2023-12-19 02:54 | 0.0863
2023-12-19 02:55 | 0.0864
2023-12-19 02:56 | 0.0863
2023-12-19 02:57 | 0.0613
2023-12-19 02:58 | 0
2023-12-19 02:59 | 0
2023-12-19 03:00 | 0
2023-12-19 03:01 | 0
2023-12-19 03:02 | 0
2023-12-19 03:03 | 0.0295
2023-12-19 03:04 | 0.0861
2023-12-19 03:05 | 0.0861
2023-12-19 03:06 | 0.0862
2023-12-19 03:07 | 0.0861
2023-12-19 03:08 | 0.0861
2023-12-19 03:09 | 0.0861
2023-12-19 03:10 | 0.0862
2023-12-19 03:11 | 0.0863
2023-12-19 03:12 | 0.0863
2023-12-19 03:13 | 0.0863
2023-12-19 03:14 | 0.0862
2023-12-19 03:15 | 0.0861
2023-12-19 03:16 | 0.0861
2023-12-19 03:17 | 0.0859
2023-12-19 03:18 | 0.086
2023-12-19 03:19 | 0.0862
2023-12-19 03:20 | 0.086
2023-12-19 03:21 | 0.0861
2023-12-19 03:22 | 0.0861
2023-12-19 03:23 | 0.0861
2023-12-19 03:24 | 0.0862
2023-12-19 03:25 | 0.0862
2023-12-19 03:26 | 0.0862
2023-12-19 03:27 | 0.0864
2023-12-19 03:28 | 0.0865
2023-12-19 03:29 | 0.0864
2023-12-19 03:30 | 0.0863
2023-12-19 03:31 | 0.0861
2023-12-19 03:32 | 0.0861
2023-12-19 03:33 | 0.086
2023-12-19 03:34 | 0.0862
2023-12-19 03:35 | 0.0861
2023-12-19 03:36 | 0.0862
2023-12-19 03:37 | 0.086
2023-12-19 03:38 | 0.086
2023-12-19 03:39 | 0.0861
2023-12-19 03:40 | 0.086
2023-12-19 03:41 | 0.086
2023-12-19 03:42 | 0.086
2023-12-19 03:43 | 0.0861
2023-12-19 03:44 | 0.0863
2023-12-19 03:45 | 0.086
2023-12-19 03:46 | 0.0862
2023-12-19 03:47 | 0.0863
2023-12-19 03:48 | 0.0863
2023-12-19 03:49 | 0.0862
2023-12-19 03:50 | 0.0863
2023-12-19 03:51 | 0.0861
2023-12-19 03:52 | 0.0862
2023-12-19 03:53 | 0.0863
2023-12-19 03:54 | 0.0863
2023-12-19 03:55 | 0.0863
2023-12-19 03:56 | 0.086
2023-12-19 03:57 | 0.0793
2023-12-19 03:58 | 0
2023-12-19 03:59 | 0
2023-12-19 04:00 | 0
2023-12-19 04:01 | 0
2023-12-19 04:02 | 0
2023-12-19 04:03 | 0.0116
2023-12-19 04:04 | 0.0859
2023-12-19 04:05 | 0.0859
2023-12-19 04:06 | 0.0861
2023-12-19 04:07 | 0.0858
2023-12-19 04:08 | 0.0859
2023-12-19 04:09 | 0.086
2023-12-19 04:10 | 0.0859
2023-12-19 04:11 | 0.0861
2023-12-19 04:12 | 0.0862
2023-12-19 04:13 | 0.0861
2023-12-19 04:14 | 0.0861
2023-12-19 04:15 | 0.0865
2023-12-19 04:16 | 0.0864
2023-12-19 04:17 | 0.0865
2023-12-19 04:18 | 0.0861
2023-12-19 04:19 | 0.0862
2023-12-19 04:20 | 0.0863
2023-12-19 04:21 | 0.0864
2023-12-19 04:22 | 0.0863
2023-12-19 04:23 | 0.0865
2023-12-19 04:24 | 0.086
2023-12-19 04:25 | 0.0862
2023-12-19 04:26 | 0.086
2023-12-19 04:27 | 0.0859
2023-12-19 04:28 | 0.086
2023-12-19 04:29 | 0.0859
2023-12-19 04:30 | 0.0862
2023-12-19 04:31 | 0.086
2023-12-19 04:32 | 0.0861
2023-12-19 04:33 | 0.0859
2023-12-19 04:34 | 0.0862
2023-12-19 04:35 | 0.0862
2023-12-19 04:36 | 0.0862
2023-12-19 04:37 | 0.0861
2023-12-19 04:38 | 0.0861
2023-12-19 04:39 | 0.086
2023-12-19 04:40 | 0.086
2023-12-19 04:41 | 0.0861
2023-12-19 04:42 | 0.0861
2023-12-19 04:43 | 0.0857
2023-12-19 04:44 | 0.0857
2023-12-19 04:45 | 0.0857
2023-12-19 04:46 | 0.0859
2023-12-19 04:47 | 0.0859
2023-12-19 04:48 | 0.086
2023-12-19 04:49 | 0.0859
2023-12-19 04:50 | 0.086
2023-12-19 04:51 | 0.0859
2023-12-19 04:52 | 0.0857
2023-12-19 04:53 | 0.0859
2023-12-19 04:54 | 0.0861
2023-12-19 04:55 | 0.0861
2023-12-19 04:56 | 0.086
2023-12-19 04:57 | 0.0862
2023-12-19 04:58 | 0.0088
2023-12-19 04:59 | 0
2023-12-19 05:00 | 0
2023-12-19 05:01 | 0
2023-12-19 05:02 | 0
2023-12-19 05:03 | 0
2023-12-19 05:04 | 0.0819
2023-12-19 05:05 | 0.0856
2023-12-19 05:06 | 0.0857
2023-12-19 05:07 | 0.0856
2023-12-19 05:08 | 0.0859
2023-12-19 05:09 | 0.0859
2023-12-19 05:10 | 0.086
2023-12-19 05:11 | 0.086
2023-12-19 05:12 | 0.0859
2023-12-19 05:13 | 0.086
2023-12-19 05:14 | 0.0857
2023-12-19 05:15 | 0.0859
2023-12-19 05:16 | 0.0859
2023-12-19 05:17 | 0.0858
2023-12-19 05:18 | 0.086
2023-12-19 05:19 | 0.086
2023-12-19 05:20 | 0.0861
2023-12-19 05:21 | 0.0862
2023-12-19 05:22 | 0.086
2023-12-19 05:23 | 0.086
2023-12-19 05:24 | 0.0861
2023-12-19 05:25 | 0.0861
2023-12-19 05:26 | 0.0865
2023-12-19 05:27 | 0.0865
2023-12-19 05:28 | 0.0865
2023-12-19 05:29 | 0.0863
2023-12-19 05:30 | 0.0865
2023-12-19 05:31 | 0.0861
2023-12-19 05:32 | 0.086
2023-12-19 05:33 | 0.0862
2023-12-19 05:34 | 0.0862
2023-12-19 05:35 | 0.0861
2023-12-19 05:36 | 0.0863
2023-12-19 05:37 | 0.0863
2023-12-19 05:38 | 0.0862
2023-12-19 05:39 | 0.0863
2023-12-19 05:40 | 0.0863
2023-12-19 05:41 | 0.0863
2023-12-19 05:42 | 0.0865
2023-12-19 05:43 | 0.0862
2023-12-19 05:44 | 0.0866
2023-12-19 05:45 | 0.0858
2023-12-19 05:46 | 0.0856
2023-12-19 05:47 | 0.0856
2023-12-19 05:48 | 0.0857
2023-12-19 05:49 | 0.0854
2023-12-19 05:50 | 0.0856
2023-12-19 05:51 | 0.0858
2023-12-19 05:52 | 0.0859
2023-12-19 05:53 | 0.0855
2023-12-19 05:54 | 0.0856
2023-12-19 05:55 | 0.0854
2023-12-19 05:56 | 0.0852
2023-12-19 05:57 | 0.0852
2023-12-19 05:58 | 0.0219
2023-12-19 05:59 | 0
2023-12-19 06:00 | 0
2023-12-19 06:01 | 0
2023-12-19 06:02 | 0
2023-12-19 06:03 | 0
2023-12-19 06:04 | 0.0679
2023-12-19 06:05 | 0.0847
2023-12-19 06:06 | 0.0844
2023-12-19 06:07 | 0.0848
2023-12-19 06:08 | 0.0848
2023-12-19 06:09 | 0.0849
2023-12-19 06:10 | 0.085
2023-12-19 06:11 | 0.0852
2023-12-19 06:12 | 0.0851
2023-12-19 06:13 | 0.0853
2023-12-19 06:14 | 0.085
2023-12-19 06:15 | 0.0852
2023-12-19 06:16 | 0.0851
2023-12-19 06:17 | 0.0851
2023-12-19 06:18 | 0.0847
2023-12-19 06:19 | 0.0841
2023-12-19 06:20 | 0.0833
2023-12-19 06:21 | 0.0836
2023-12-19 06:22 | 0.084
2023-12-19 06:23 | 0.0844
2023-12-19 06:24 | 0.084
2023-12-19 06:25 | 0.0843
2023-12-19 06:26 | 0.0844
2023-12-19 06:27 | 0.0843
2023-12-19 06:28 | 0.0847
2023-12-19 06:29 | 0.0844
2023-12-19 06:30 | 0.0847
2023-12-19 06:31 | 0.0845
2023-12-19 06:32 | 0.0853
2023-12-19 06:33 | 0.0851
2023-12-19 06:34 | 0.0851
2023-12-19 06:35 | 0.085
2023-12-19 06:36 | 0.085
2023-12-19 06:37 | 0.0846
2023-12-19 06:38 | 0.0847
2023-12-19 06:39 | 0.0849
2023-12-19 06:40 | 0.0848
2023-12-19 06:41 | 0.0851
2023-12-19 06:42 | 0.085
2023-12-19 06:43 | 0.0856
2023-12-19 06:44 | 0.0853
2023-12-19 06:45 | 0.0853
2023-12-19 06:46 | 0.085
2023-12-19 06:47 | 0.085
2023-12-19 06:48 | 0.0851
2023-12-19 06:49 | 0.085
2023-12-19 06:50 | 0.0852
2023-12-19 06:51 | 0.0848
2023-12-19 06:52 | 0.0854
2023-12-19 06:53 | 0.0856
2023-12-19 06:54 | 0.0857
2023-12-19 06:55 | 0.0858
2023-12-19 06:56 | 0.0855
2023-12-19 06:57 | 0.0854
2023-12-19 06:58 | 0.0396
2023-12-19 06:59 | 0
2023-12-19 07:00 | 0
2023-12-19 07:01 | 0
2023-12-19 07:02 | 0
2023-12-19 07:03 | 0
2023-12-19 07:04 | 0.0498
2023-12-19 07:05 | 0.0853
2023-12-19 07:06 | 0.0851
2023-12-19 07:07 | 0.0851
2023-12-19 07:08 | 0.0855
2023-12-19 07:09 | 0.0855
2023-12-19 07:10 | 0.0853
2023-12-19 07:11 | 0.0854
2023-12-19 07:12 | 0.0861
2023-12-19 07:13 | 0.086
2023-12-19 07:14 | 0.0859
2023-12-19 07:15 | 0.0855
2023-12-19 07:16 | 0.0858
2023-12-19 07:17 | 0.0858
2023-12-19 07:18 | 0.0855
2023-12-19 07:19 | 0.0852
2023-12-19 07:20 | 0.0858
2023-12-19 07:21 | 0.0861
2023-12-19 07:22 | 0.0857
2023-12-19 07:23 | 0.0857
2023-12-19 07:24 | 0.0858
2023-12-19 07:25 | 0.0858
2023-12-19 07:26 | 0.0858
2023-12-19 07:27 | 0.0859
2023-12-19 07:28 | 0.086
2023-12-19 07:29 | 0.0857
2023-12-19 07:30 | 0.0857
2023-12-19 07:31 | 0.0859
2023-12-19 07:32 | 0.086
2023-12-19 07:33 | 0.0859
2023-12-19 07:34 | 0.0855
2023-12-19 07:35 | 0.0856
2023-12-19 07:36 | 0.0856
2023-12-19 07:37 | 0.0859
2023-12-19 07:38 | 0.0859
2023-12-19 07:39 | 0.086
2023-12-19 07:40 | 0.0859
2023-12-19 07:41 | 0.0859
2023-12-19 07:42 | 0.0859
2023-12-19 07:43 | 0.0861
2023-12-19 07:44 | 0.0861
2023-12-19 07:45 | 0.0859
2023-12-19 07:46 | 0.0858
2023-12-19 07:47 | 0.0858
2023-12-19 07:48 | 0.0856
2023-12-19 07:49 | 0.0855
2023-12-19 07:50 | 0.0856
2023-12-19 07:51 | 0.0858
2023-12-19 07:52 | 0.0856
2023-12-19 07:53 | 0.0856
2023-12-19 07:54 | 0.0858
2023-12-19 07:55 | 0.0858
2023-12-19 07:56 | 0.0859
2023-12-19 07:57 | 0.0861
2023-12-19 07:58 | 0.0701
2023-12-19 07:59 | 0
2023-12-19 08:00 | 0
2023-12-19 08:01 | 0
2023-12-19 08:02 | 0
2023-12-19 08:03 | 0
2023-12-19 08:04 | 0.0192
2023-12-19 08:05 | 0.0858
2023-12-19 08:06 | 0.0859
2023-12-19 08:07 | 0.0857
2023-12-19 08:08 | 0.086
2023-12-19 08:09 | 0.0858
2023-12-19 08:10 | 0.0855
2023-12-19 08:11 | 0.0856
2023-12-19 08:12 | 0.0856
2023-12-19 08:13 | 0.0857
2023-12-19 08:14 | 0.0854
2023-12-19 08:15 | 0.0855
2023-12-19 08:16 | 0.0856
2023-12-19 08:17 | 0.0857
2023-12-19 08:18 | 0.0858
2023-12-19 08:19 | 0.0853
2023-12-19 08:20 | 0.0855
2023-12-19 08:21 | 0.0857
2023-12-19 08:22 | 0.0858
2023-12-19 08:23 | 0.0863
2023-12-19 08:24 | 0.0863
2023-12-19 08:25 | 0.0863
2023-12-19 08:26 | 0.0861
2023-12-19 08:27 | 0.086
2023-12-19 08:28 | 0.0862
2023-12-19 08:29 | 0.0862
2023-12-19 08:30 | 0.0862
2023-12-19 08:31 | 0.0861
2023-12-19 08:32 | 0.086
2023-12-19 08:33 | 0.086
2023-12-19 08:34 | 0.0858
2023-12-19 08:35 | 0.0858
2023-12-19 08:36 | 0.0858
2023-12-19 08:37 | 0.0858
2023-12-19 08:38 | 0.0859
2023-12-19 08:39 | 0.0859
2023-12-19 08:40 | 0.0855
2023-12-19 08:41 | 0.0859
2023-12-19 08:42 | 0.0858
2023-12-19 08:43 | 0.0861
2023-12-19 08:44 | 0.0862
2023-12-19 08:45 | 0.0862
2023-12-19 08:46 | 0.0862
2023-12-19 08:47 | 0.086
2023-12-19 08:48 | 0.0859
2023-12-19 08:49 | 0.086
2023-12-19 08:50 | 0.0862
2023-12-19 08:51 | 0.086
2023-12-19 08:52 | 0.086
2023-12-19 08:53 | 0.0862
2023-12-19 08:54 | 0.0865
2023-12-19 08:55 | 0.0862
2023-12-19 08:56 | 0.0863
2023-12-19 08:57 | 0.0859
2023-12-19 08:58 | 0.0857
2023-12-19 08:59 | 0.0132
2023-12-19 09:00 | 0
2023-12-19 09:01 | 0
2023-12-19 09:02 | 0
2023-12-19 09:03 | 0
2023-12-19 09:04 | 0
2023-12-19 09:05 | 0.0764
2023-12-19 09:06 | 0.0861
2023-12-19 09:07 | 0.086
2023-12-19 09:08 | 0.0855
2023-12-19 09:09 | 0.0855
2023-12-19 09:10 | 0.0862
2023-12-19 09:11 | 0.0862
2023-12-19 09:12 | 0.0863
2023-12-19 09:13 | 0.0856
2023-12-19 09:14 | 0.0854
2023-12-19 09:15 | 0.0862
2023-12-19 09:16 | 0.0868
2023-12-19 09:17 | 0.0866
2023-12-19 09:18 | 0.0865
2023-12-19 09:19 | 0.0866
2023-12-19 09:20 | 0.0862
2023-12-19 09:21 | 0.0859
2023-12-19 09:22 | 0.0858
2023-12-19 09:23 | 0.0856
2023-12-19 09:24 | 0.0858
2023-12-19 09:25 | 0.0859
2023-12-19 09:26 | 0.0862
2023-12-19 09:27 | 0.0859
2023-12-19 09:28 | 0.0859
2023-12-19 09:29 | 0.0857
2023-12-19 09:30 | 0.086
2023-12-19 09:31 | 0.0864
2023-12-19 09:32 | 0.0865
2023-12-19 09:33 | 0.0858
2023-12-19 09:34 | 0.0864
2023-12-19 09:35 | 0.0862
2023-12-19 09:36 | 0.0861
2023-12-19 09:37 | 0.0864
2023-12-19 09:38 | 0.0864
2023-12-19 09:39 | 0.0861
2023-12-19 09:40 | 0.0863
2023-12-19 09:41 | 0.0865
2023-12-19 09:42 | 0.0865
2023-12-19 09:43 | 0.086
2023-12-19 09:44 | 0.0864
2023-12-19 09:45 | 0.0861
2023-12-19 09:46 | 0.0862
2023-12-19 09:47 | 0.0861
2023-12-19 09:48 | 0.0861
2023-12-19 09:49 | 0.0859
2023-12-19 09:50 | 0.0858
2023-12-19 09:51 | 0.0864
2023-12-19 09:52 | 0.086
2023-12-19 09:53 | 0.0858
2023-12-19 09:54 | 0.0862
2023-12-19 09:55 | 0.0861
2023-12-19 09:56 | 0.086
2023-12-19 09:57 | 0.0866
2023-12-19 09:58 | 0.0863
2023-12-19 09:59 | 0.0416
2023-12-19 10:00 | 0
2023-12-19 10:01 | 0
2023-12-19 10:02 | 0
2023-12-19 10:03 | 0
2023-12-19 10:04 | 0
2023-12-19 10:05 | 0.0481
2023-12-19 10:06 | 0.0853
2023-12-19 10:07 | 0.0856
2023-12-19 10:08 | 0.0857
2023-12-19 10:09 | 0.0853
2023-12-19 10:10 | 0.0859
2023-12-19 10:11 | 0.0856
2023-12-19 10:12 | 0.0853
2023-12-19 10:13 | 0.0859
2023-12-19 10:14 | 0.0857
2023-12-19 10:15 | 0.0861
2023-12-19 10:16 | 0.0858
2023-12-19 10:17 | 0.0856
2023-12-19 10:18 | 0.0858
2023-12-19 10:19 | 0.0861
2023-12-19 10:20 | 0.0858
2023-12-19 10:21 | 0.0861
2023-12-19 10:22 | 0.0862
2023-12-19 10:23 | 0.0866
2023-12-19 10:24 | 0.0864
2023-12-19 10:25 | 0.0858
2023-12-19 10:26 | 0.086
2023-12-19 10:27 | 0.0864
2023-12-19 10:28 | 0.086
2023-12-19 10:29 | 0.0861
2023-12-19 10:30 | 0.0861
2023-12-19 10:31 | 0.0861
2023-12-19 10:32 | 0.0854
2023-12-19 10:33 | 0.0855
2023-12-19 10:34 | 0.086
2023-12-19 10:35 | 0.0861
2023-12-19 10:36 | 0.0863
2023-12-19 10:37 | 0.0865
2023-12-19 10:38 | 0.0865
2023-12-19 10:39 | 0.0862
2023-12-19 10:40 | 0.0861
2023-12-19 10:41 | 0.086
2023-12-19 10:42 | 0.0865
2023-12-19 10:43 | 0.0861
2023-12-19 10:44 | 0.0861
2023-12-19 10:45 | 0.0863
2023-12-19 10:46 | 0.0867
2023-12-19 10:47 | 0.086
2023-12-19 10:48 | 0.0864
2023-12-19 10:49 | 0.0866
2023-12-19 10:50 | 0.0865
2023-12-19 10:51 | 0.0864
2023-12-19 10:52 | 0.0862
2023-12-19 10:53 | 0.0859
2023-12-19 10:54 | 0.0862
2023-12-19 10:55 | 0.086
2023-12-19 10:56 | 0.0861
2023-12-19 10:57 | 0.0865
2023-12-19 10:58 | 0.086
2023-12-19 10:59 | 0.0708
2023-12-19 11:00 | 0
2023-12-19 11:01 | 0
2023-12-19 11:02 | 0
2023-12-19 11:03 | 0
2023-12-19 11:04 | 0
2023-12-19 11:05 | 0.0183
2023-12-19 11:06 | 0.086
2023-12-19 11:07 | 0.0861
2023-12-19 11:08 | 0.0863
2023-12-19 11:09 | 0.086
2023-12-19 11:10 | 0.0859
2023-12-19 11:11 | 0.0849
2023-12-19 11:12 | 0.085
2023-12-19 11:13 | 0.0856
2023-12-19 11:14 | 0.0865
2023-12-19 11:15 | 0.0869
2023-12-19 11:16 | 0.0864
2023-12-19 11:17 | 0.086
2023-12-19 11:18 | 0.0864
2023-12-19 11:19 | 0.0862
2023-12-19 11:20 | 0.0862
2023-12-19 11:21 | 0.086
2023-12-19 11:22 | 0.0856
2023-12-19 11:23 | 0.0857
2023-12-19 11:24 | 0.0856
2023-12-19 11:25 | 0.0854
2023-12-19 11:26 | 0.0862
2023-12-19 11:27 | 0.0864
2023-12-19 11:28 | 0.0864
2023-12-19 11:29 | 0.0857
2023-12-19 11:30 | 0.0861
2023-12-19 11:31 | 0.0864
2023-12-19 11:32 | 0.086
2023-12-19 11:33 | 0.0857
2023-12-19 11:34 | 0.0856
2023-12-19 11:35 | 0.086
2023-12-19 11:36 | 0.0856
2023-12-19 11:37 | 0.0858
2023-12-19 11:38 | 0.0861
2023-12-19 11:39 | 0.086
2023-12-19 11:40 | 0.086
2023-12-19 11:41 | 0.0861
2023-12-19 11:42 | 0.086
2023-12-19 11:43 | 0.086
2023-12-19 11:44 | 0.0859
2023-12-19 11:45 | 0.0861
2023-12-19 11:46 | 0.086
2023-12-19 11:47 | 0.0856
2023-12-19 11:48 | 0.0859
2023-12-19 11:49 | 0.0865
2023-12-19 11:50 | 0.0866
2023-12-19 11:51 | 0.0868
2023-12-19 11:52 | 0.0865
2023-12-19 11:53 | 0.0861
2023-12-19 11:54 | 0.0862
2023-12-19 11:55 | 0.0863
2023-12-19 11:56 | 0.0867
2023-12-19 11:57 | 0.0868
2023-12-19 11:58 | 0.0865
2023-12-19 11:59 | 0.0866
2023-12-19 12:00 | 0.0184
2023-12-19 12:01 | 0
2023-12-19 12:02 | 0
2023-12-19 12:03 | 0
2023-12-19 12:04 | 0
2023-12-19 12:05 | 0
2023-12-19 12:06 | 0.0698
2023-12-19 12:07 | 0.085
2023-12-19 12:08 | 0.0854
2023-12-19 12:09 | 0.086
2023-12-19 12:10 | 0.0858
2023-12-19 12:11 | 0.0851
2023-12-19 12:12 | 0.0856
2023-12-19 12:13 | 0.0856
2023-12-19 12:14 | 0.0862
2023-12-19 12:15 | 0.0858
2023-12-19 12:16 | 0.086
2023-12-19 12:17 | 0.0855
2023-12-19 12:18 | 0.0857
2023-12-19 12:19 | 0.0856
2023-12-19 12:20 | 0.0854
2023-12-19 12:21 | 0.0857
2023-12-19 12:22 | 0.086
2023-12-19 12:23 | 0.0859
2023-12-19 12:24 | 0.0863
2023-12-19 12:25 | 0.0863
2023-12-19 12:26 | 0.0859
2023-12-19 12:27 | 0.0861
2023-12-19 12:28 | 0.0863
2023-12-19 12:29 | 0.0862
2023-12-19 12:30 | 0.0856
2023-12-19 12:31 | 0.0859
2023-12-19 12:32 | 0.0859
2023-12-19 12:33 | 0.0863
2023-12-19 12:34 | 0.0864
2023-12-19 12:35 | 0.0862
2023-12-19 12:36 | 0.0862
2023-12-19 12:37 | 0.0862
2023-12-19 12:38 | 0.0859
2023-12-19 12:39 | 0.0862
2023-12-19 12:40 | 0.0859
2023-12-19 12:41 | 0.0857
2023-12-19 12:42 | 0.0855
2023-12-19 12:43 | 0.0858
2023-12-19 12:44 | 0.0858
2023-12-19 12:45 | 0.0855
2023-12-19 12:46 | 0.0854
2023-12-19 12:47 | 0.0853
2023-12-19 12:48 | 0.0852
2023-12-19 12:49 | 0.085
2023-12-19 12:50 | 0.0852
2023-12-19 12:51 | 0.0851
2023-12-19 12:52 | 0.0854
2023-12-19 12:53 | 0.0853
2023-12-19 12:54 | 0.0856
2023-12-19 12:55 | 0.0856
2023-12-19 12:56 | 0.0862
2023-12-19 12:57 | 0.0863
2023-12-19 12:58 | 0.0858
2023-12-19 12:59 | 0.086
2023-12-19 13:00 | 0.0537
2023-12-19 13:01 | 0
2023-12-19 13:02 | 0
2023-12-19 13:03 | 0
2023-12-19 13:04 | 0
2023-12-19 13:05 | 0
2023-12-19 13:06 | 0.0346
2023-12-19 13:07 | 0.0843
2023-12-19 13:08 | 0.0846
2023-12-19 13:09 | 0.0859
2023-12-19 13:10 | 0.0859
2023-12-19 13:11 | 0.0856
2023-12-19 13:12 | 0.0851
2023-12-19 13:13 | 0.0854
2023-12-19 13:14 | 0.0854
2023-12-19 13:15 | 0.0854
2023-12-19 13:16 | 0.0855
2023-12-19 13:17 | 0.0859
2023-12-19 13:18 | 0.086
2023-12-19 13:19 | 0.0861
2023-12-19 13:20 | 0.0859
2023-12-19 13:21 | 0.0859
2023-12-19 13:22 | 0.0861
2023-12-19 13:23 | 0.0857
2023-12-19 13:24 | 0.0861
2023-12-19 13:25 | 0.0862
2023-12-19 13:26 | 0.0859
2023-12-19 13:27 | 0.086
2023-12-19 13:28 | 0.0857
2023-12-19 13:29 | 0.086
2023-12-19 13:30 | 0.0861
2023-12-19 13:31 | 0.0861
2023-12-19 13:32 | 0.0861
2023-12-19 13:33 | 0.0861
2023-12-19 13:34 | 0.0861

## Notes Manuals
https://tsi.com/products/ventilation-test-instruments/alnor/alnor-capture-hoods/alnor-balometer-capture-hood-ebt731/
Alnor EBT731
Page 56
In most cases, backpressure compensated measurements will provide the most satisfactory flow measurement results, especially when the flow is greater than 500 cfm.
Page 61
Always recommended to do a traverse.
Note that our vents are 3.5 inches by 11 with grill -- the balometer is over a square foot with limited obstructions
Specs:
https://tsi.com/getmedia/5278d366-3c69-4a5d-b8c2-5dc48da3883d/EBT730-731_US_5001434?ext=.pdf
Accuracy claim
±3% of reading ±12 m3/h (±7 ft3/min) at flows >85 m3/h (>50 ft3/min)
So, we are measuring at the low end of the accuracy
Note that this appears to be an accuracy claim and a precision claim -- within 3% of true and some variability around the answer.
https://tsi.com/getmedia/f8e47cbe-dbe2-423d-b695-b2a2fda2503b/TSI-109?ext=.pdf
Converting Standard Velocity to Actual Velocity Application Note (TSI-109) A4
Standard vs actual velocity
Higher temperature in supplyi ducts might raise velocity measurements? Assume corrected already
Spec sheet says "Automatic density correction -- has temp and pressure"
https://www.daikinac.com/content/assets/DOC/EngineeringManuals/2017/Engineering%20Manual-SkyAir-web.pdf
Motor out put up to 350w
Airflow 635/583/529
Duct pressure 0.4, 0.2 to 0.8 -- changeable in 14 stages by remote controller
| Full load ampacity is 1.3 low vs kw | 286
p.95 charts suggest kw at 32 degrees outside and 61 inside should be 2.09
p.104 and 113 suggest operating range between 545 and 740 depending on settings for static pressure
Fan Curves on 14 alternative install settings for duct pressure -- guessing we are on lowest curve

## Density
https://www.techstreet.com/ashrae/standards/f01-psychrometrics-i-p?product_id=2225687
Consider our return air to be 65F and 45%RH, which translates in to moisture content of 45 grains, using this table: | [7 empty] | https://www.engineeringtoolbox.com/water-vapor-air-d_854.html
| 0.0064286 | Ws | Roughly 50% of saturation weight
Table 2 Thermodynamic Properties of Saturated Moist and Dry Air at Standard Atmospheric Pressure, 14.696 psia (Continued)
|  | Ft3/lb(da) | [7 empty] | Consider our air to be 65F and 45%RH
| lbw/lbda = Ws | V dry | v sat | H dry | H sat | Capacity dry | Capacity Sat
60 | 0.011089 | 13.096 | 13.328 | 14.412 | 26.467 | 0.2403 | 0.2426
61 | 0.011498 | 13.121 | 13.363 | 14.653 | 27.156 | 0.2403 | 0.2427
62 | 0.011921 | 13.146 | 13.397 | 14.893 | 27.861 | 0.2403 | 0.2428
63 | 0.012357 | 13.171 | 13.432 | 15.133 | 28.581 | 0.2403 | 0.2429 | 0.2416
64 | 0.012807 | 13.197 | 13.468 | 15.373 | 29.317 | 0.2403 | 0.243
65 | 0.013272 | 13.222 | 13.503 | 15.614 | 30.07 | 0.2403 | 0.2431 | 0.2417
66 | 0.013753 | 13.247 | 13.539 | 15.854 | 30.839 | 0.2403 | 0.2432
67 | 0.014249 | 13.272 | 13.576 | 16.094 | 31.626 | 0.2403 | 0.2433
68 | 0.014761 | 13.298 | 13.612 | 16.335 | 32.431 | 0.2403 | 0.2434
69 | 0.015289 | 13.323 | 13.649 | 16.575 | 33.254 | 0.2403 | 0.2435
Water vapor density at saturation
Density (lb dry air/ft3) |  | dry | sat dry portion only | Sat mix weight | avg sat/dry |  | ft3/lb | lb/ft3 | weight percent sat at vaolume
60 |  | 0.076359 | 0.07503 | 0.075862 | 0.076111 | 60 | 1206.1 | 0.00082912 | 1.105%
61 |  | 0.076214 | 0.074833 | 0.075694 | 0.075954 | 61 | 1166.2 | 0.00085749 | 1.146%
62 |  | 0.076069 | 0.074644 | 0.075533 | 0.075801 | 62 | 1127.7 | 0.00088676 | 1.188%
63 |  | 0.075924 | 0.074449 | 0.075369 | 0.075647 | 63 | 1090.7 | 0.00091684 | 1.232%
64 |  | 0.075775 | 0.07425 | 0.075201 | 0.075488 | 64 | 1055.1 | 0.00094778 | 1.276%
65 |  | 0.075632 | 0.074058 | 0.075041 | 0.075336 | 65 | 1020.8 | 0.00097962 | 1.323%
66 |  | 0.075489 | 0.073861 | 0.074877 | 0.075183 | 66 | 987.77 | 0.0010124 | 1.371%
67 |  | 0.075347 | 0.073659 | 0.074709 | 0.075028 | 67 | 955.93 | 0.0010461 | 1.42%
68 |  | 0.075199 | 0.073465 | 0.074549 | 0.074874 | 68 | 925.25 | 0.0010808 | 1.471%
69 |  | 0.075058 | 0.073265 | 0.074386 | 0.074722 | 69 | 895.68 | 0.0011165 | 1.524%
Values from Tables
| Sat Water vapor alone ft3/lb | 1206.1
| sat Air and water/LBDRY | 13.328
| Air only (DRY) | 13.096
| lbw/lbda = Ws | 0.011089
Indentity check
| Sat mix with 1 lb air | 1 | Has 1lb of air
| will have water of | 0.011089 | Water weight from ratio
| Total weight | 1.0111 | Mixture containing 1 lb air, total weight
| Specific volume /lb dry air | 13.328 | Same as table, sincce denominator is dry air
| Water Weight in 1 ft3 of mix | 0.00082912 | Reading table 3 Vg as volume of the mix that contains 1lb water (saturated) -- not really correct -- says Vg is for steam
| Water weight in vol | 0.01105 | Checks? Is the small difference due to thte saturated water vapor pressure enhancement factor (
| % difference | 0.99653 | 1.005 | 1.0015
At saturation
Hi and low barometric pressure at Logan in 2023 vs standard pressure.
[10 empty] | 28.9 | 30.6 | 29.921 | -0.034123 | 0.022693
[5 empty] | Standard pressure | 1013.25 | 29.92 | millibar, mercury |  | https://www.wunderground.com/history/monthly/us/ma/east-boston/KBOS/date/2023-12
|  |  | 0.2417 |  |  |  | 29.62 |  |  | https://en.wikipedia.org/wiki/Atmospheric_pressure
0.0753
60
1.092
https://barometricpressure.app/content/understanding-high-low-pressure-readings#google_vignette
What is high or low barometric pressure? Adjusted to sea level, a pressure reading above 30.2 inHg is considered to be high pressure, and below 29.8 inHg is considered low. Most of the time, in human-inhabited places, the barometric pressure will stay close to the normal range (29.8 inHg-30.2 inHg), and will rarely exceed 30.5 inHg or fall below 29.4 inHg. The average barometric pressure is 29.92 inHg (or 1 atmosphere!). In summary:

## Misc Notes
Generally:
https://www.engineeringtoolbox.com/air-psychrometrics-properties-t_8.html
By weight moisture content of air is < 1%
Grains (1/7000 of a pound) = 66 if 60% humidity (heavy rain) at 70 degrees
https://www.engineeringtoolbox.com/water-vapor-air-d_854.html
Molier Chart yields Enthalpy from RH and Temp
https://www.engineeringtoolbox.com/psychrometric-chart-mollier-d_27.html
Components of enthalpy of moist air
Specific heat of dry air
= 0.240 (Btu/lboF)
Sesnsible specific heat of the water vapor
0.444 (Btu/lboF)
Evaporation heat -- is not increased with temperature
1061 (Btu/lb)
Complete formula (where x is moisture content by weight)
h = (0.240 Btu/lboF) t + x [(0.444 Btu/lboF) t + (1061 Btu/lb)]
Note! - the latent heat due to evaporation of water is the major part of the enthalpy. The sensible heat due to heating evaporated water vapor can be almost neglected.
BUT FURTHER
In heating, the last term simplifies out of the delta (although it is large absolutely) because it is not a function of temperature so:
https://en.wiktionary.org/wiki/humid_heat#:~:text=In%20U.S.%20customary%20units%2C%20c,dry%20air%20in%20the%20mixture.
cs = 0.24 + 0.45H where 0.24 BTU/lb°F is the heat capacity of dry air, 0.45 BTU/lb°F is the heat capacity of water vapor, and H is the specific humidity in lb water vapor per lb dry air in the mixture.
https://chem.libretexts.org/Bookshelves/Introductory_Chemistry/Introductory_Chemistry_(CK-12)/17%3A_Thermochemistry/17.04%3A_Heat_Capacity_and_Specific_Heat#:~:text=Heat%20capacity%20is%20the%20amount,substance%20by%201oC.
Further, in heating, since x < 0.01 (H in the wiktionary version), this term is also within the noise level
Since x < 0.01 (H in the wiktionary version), this term is also within the noise level
https://www.engineeringtoolbox.com/heating-humid-air-d_693.html
https://www.engineeringtoolbox.com/enthalpy-moist-air-d_683.html
dh A-B = c pa ( t B - t A ) (2b)
https://en.wikipedia.org/wiki/Density_of_air
At 101.325 kPa (abs) and 20 °C (68 °F), air has a density of approximately 1.204 kg/m3 (0.0752 lb/cu ft)
At 101.325 kPa (abs) and 15 °C (59 °F), air has a density of approximately 1.225 kg/m3 (0.0765 lb/cu ft),
note, could vary this is an formula, but using .076 is a good plug (again within one percent)
Can summarize to single term
| 60 | min/hr
| 0.24 | BTU/lb-F
| 0.076 | lb/ft^3
| 1.0944 | BTU/hr / cfm - F
This compares within rounding error to David Korn's note: I use the sensible (heating) formula "1.08 BTUH/CFM-F"
Summarizing cfm vs. delta T -- 120 | 12-18,6:30 | 12-18,7AM | 12-08,7:23 | 12-20, 6:40AM | 12-22, 7:40AM
Delta temperature degrees | 30 | 31 | 40 | 39 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Constant specific heat (BTU/(lb deg F) | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
Delta energy (Btu/lb) | 7.2 | 7.44 | 9.6 | 9.36 | 9.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minutes per hour | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Volume Cubic feet per minute | 580 | 580 | 650 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
Pounds per cubic foot | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076
Delta energy per hour (BTU/hr) | 19042.56 | 19677.312 | 28454.4 | 24755.328 | 26024.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTU/kwh | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412
kilowatts of heat energy per hour | 5.5811 | 5.7671 | 8.3395 | 7.2554 | 7.6274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sample kwh compressor | 1014 | 1603 | 3475 | 2709 | 3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sample kwh fan | 90.6 | 96.8 | 101 | 100 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Instantaneous COP! | 5.0526 | 3.3928 | 2.3321 | 2.5829 | 2.2714 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Outdoor temperature | 60.6 | 40.3 | 26 | 30 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summarizing cfm vs. delta T -- 118 | 12-18,8 | 12-19,7:20 |  | 12-20, 6:40AM | 12-22, 7:40AM
Delta temperature degrees | 27 | 30 | 0 | 42 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Constant specific heat (BTU/(lb deg F) | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
Delta energy (Btu/lb) | 6.48 | 7.2 | 0 | 10.08 | 9.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minutes per hour | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Volume Cubic feet per minute | 720 | 720 | 720 | 720 | 720 | 720 | 720 | 720 | 720 | 720 | 720 | 720 | 720
Pounds per cubic foot | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076
Delta energy per hour (BTU/hr) | 21275.136 | 23639.04 | 0 | 33094.656 | 32306.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTU/kwh | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412 | 3412
kilowatts of heat energy per hour | 6.2354 | 6.9282 | 0 | 9.6995 | 9.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sample kwh compressor | 820 | 1450 | 0 | 2960 | 3308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sample kwh fan | 90.6 | 92 | 0 | 95.2 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Instantaneous COP! | 6.8476 | 4.493 | #DIV/0! | 3.1747 | 2.7791 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Outdoor temperature | 60.6 | 40.3 | 0 | 30 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Vent is close to clear (hidden)
NOTE: MEASURED INTERIOR DIAMETER WITHIN FLANGE IS 12 OR EVEN SLIGHTLY ABOVE -- CONSIDER 144 GOOD.
PLACING extended tape in within opening, could feel a little bit of play, even resting on flange, slightly above 12" diameter.

## NO ERV connect to HVAC (hidden)
Is it coincidence that get lower readings when ERV in 118 is on?
With ERV on and system off, find zero flow in system vents
Kitchen
Gym
Study return
Bathroom
Bedroom vent
Bedroom return
Living room
Hall
Basement
Dining room return
Can find no difference in barometric pressure when ERV on or off and in different rooms (study vs bath vs dining room)
(Just setting unhooded balometer on ground and reading zero flow but also pressure)
Tracing ERV ducts, can mostly follow
Supply to Bedroom, Study, Gym
Return from bathrooms
External intake and exhaust
Hard to imagine any hidden branches