## Consolidating Estimates
Summary of flow measurements from all instruments
| Results discarded as to scale, but not as to relative shares |  |  |  |  | Results accepted as to scale
Ducts | Alnor EBT731 Balometer with Back Pressure Correction | Alnor EBT731 Balometer w/o back pressure | Testo 417 Rotating vane anemometer at grills (no k factor for grill) | Alnor 6200 Low Flow Balometer | Testo 415 Hot Wire Anemometer @ Return Plenum | Duct traverse with Testo 415 Hot wire anemometer | Duct traverse with Alnor EBT731 as manometer with Pitot tube
Basement | 161.5 | 120.8 | 118 | 75
Bathroom | 76 | 55.8 | 50 | 32.5 |  | 46.0104 | 42.3398
Study | 175.5 | 129.3 | 126 | 93
Kitchen | 100 | 97.2 | 111 | 72 |  | 101 | 57.7268
Dining Room | 75 | 61.9 | 57 | 42.5 |  | 46 | 39.3381
Living Room | 75 | 73.3 | 61 | 41.5
Gym | 101.5 | 63.3 | 70 | 46 |  | 56.6 | 50.92
Hall | 86 | 73.9 | 61 | 44.5
Bedroom | 70 | 43.2 | 41 | 32 |  |  | 29.2479
Total | 920.5 | 718.6 | 693.23 | 479 | 694 | 592.6104 | 545.3339
West Branch: Basement, study, kitchen | 437 | 347.3 | 355 | 240 |  | 294.6 | 267.9052
East Branch: Dining, gym, living, hall, bed | 407.5 | 315.6 | 290 | 206.5 |  | 252 | 235.0889
East sub branch: Living, Hall | 161 | 147.2 | 122 | 86 |  |  | 96.2222
Sum of East branch components | 407.5 | 315.6 | 290 | 206.5 |  |  | 215.7282
Note, missing quantities imputed from Balometer center 4 proportions
Note, measurements constructed as sum of other measurements
Observations:
(0) In general, the relative shares of ducts remains consistent (see share analysis below)
(1) Pitot traverse very low for kitchen -- high turbulence (big flow swing in small pipe)? Anemometer is relatively high (too large a share of branch), likely for same reason.
Actually, in the share analysis, all the small round ducts come in relatively low. Some kind of measurement effect. See discussion of pointwise comparisons for rectangular.
(2) None of the Pitot measurements meet standard for consistency across plane -- likely low because of turbulence; on the other hand anemometer could be high for same.
(3) The east branch components do not quite add up.
(4) The two traverse methods yield similar results -- within 10%: Consider that the range of possible results.
(5) Note that rated value for high high on fan is targeted at 635.
SCALE MEASUREMENT DISCARD REASONS
(1) Back pressure correction not appropriate -- balometer opening wider/clearer than diffusers and often get no difference error; recommended for flows over 500
(2) Balometer without back pressure correction still suffers from inflation due to grid averaging of varying velocity pressure; also manual recommends traverse for calibration.
(3) Rotating vane anemometer low precision as to area capture; no grill adjustment factor.
(4) Lo flow is very low -- surprisingly so. It is a different mechanism than the EBT731 balometer -- it has a longer chimney. But manual discounts absolute values and recommends traverse.
(5) Hot wire in plenum inflated due to turbulence -- hot wire captures all cross and reverse currents.
Values as % of total where present
Basement | 17.54% | 16.81% | 17.02% | 15.66%
Bathroom | 8.256% | 7.765% | 7.213% | 6.785%
Study | 19.07% | 17.99% | 18.18% | 19.42%
Kitchen | 10.86% | 13.53% | 16.01% | 15.03% |  | 17.04% | 10.59%
Dining Room | 8.148% | 8.614% | 8.222% | 8.873% |  | 7.762% | 7.214%
Living Room | 8.148% | 10.2% | 8.799% | 8.664%
Gym | 11.03% | 8.809% | 10.1% | 9.603% |  | 9.551% | 9.337%
Hall | 9.343% | 10.28% | 8.799% | 9.29%
Bedroom | 7.605% | 6.012% | 5.914% | 6.681% |  |  | 5.363%
Total | 100% | 100% | 100% | 100% | 100% | 100% | 100%
West Branch: Basement, study, kitchen | 47.47% | 48.33% | 51.21% | 50.1% |  | 49.71% | 49.13%
East Branch: Dining, gym, living, hall, bed | 44.27% | 43.92% | 41.83% | 43.11% |  | 42.52% | 43.11%
East sub branch: Living, Hall | 17.49% | 20.48% | 17.6% | 17.95% |  |  | 17.64%
Sum of East branch components | 44.27% | 43.92% | 41.83% | 43.11% |  |  | 39.56%
Instrument | # of measurement passes
Alnor EBT731 Balometer with Back Pressure Correction | Single pass
Alnor EBT731 Balometer w/o back pressure | Showing average of center 4 out of 6 for each duct
Testo 417 Rotating vane anemometer at grills | Single pass
Alnor 6200 Low Flow Balometer | Average of two passes for each duct
Testo 415 Hot Wire Anemometer @ Return Plenum | Showing average of center 3 measurements point-wise from 5
Testo 415 Hot wire anemometer traverse of supply ducts | Mostly single pass per duct
Duct traverse with Alnor EBT731 as manometer with Pitot tube | Two to three traverses per duct, averaged

## Flow vs Watts
Looking at start up stages -- watts vs flow
Location | Watts | Average flow
Kitchen vent with balometer (cfm) | 38 | 85.3333 | 62.52% | 36.7367 | 84 | 84 | 83 | 87 | 85 | 89 | `
Kitchen vent with balometer (cfm) | 60 | 111.5 | 81.68% | 62.7209 | 111 | 112
Kitchen vent with balometer (cfm) | 94 | 136.5 | 100% | 94 | 139 | 136 | 132 | 139
Redo 1 Kitchen vent with balometer (cfm) | 38 | 77 | 62.47% | 36.689 | 75 | 75 | 79 | 79
Redo 1 Kitchen vent with balometer (cfm) | 60 | 102.5 | 83.16% | 65.0132 | 100 | 105
Redo 1 Kitchen vent with balometer (cfm) | 94 | 123.25 | 100% | 94 | 117 | 128 | 127 | 121
Pitot in large supply vent center cell (fpm) | 38 | 431 | 68.96% | 44.7015 | 11 samples (355 to 560)
Pitot in large supply vent center cell (fpm) | 60 | 533 | 85.28% | 68.3632 | 6 samples (499-584)
Pitot in large supply vent center cell (fpm) | 94 | 625 | 100% | 94 | 11 samples (574-680)
This is consistent with ESP drop |  | Pressure drop | Sqr Root Pressure | Fan power drop | Squre root fan power
| 38 | 43.33% | 65.82% | 40.43% | 0.63581
| 60 | 68.45% | 82.73% | 63.83% | 0.79894
| 94 | 100% | 100% | 100% | 1
Power levels as % of full power -- 38 CFM

## Balometer wrinkles
Balometer placement matters
Using rectangular hood
| 116, 117 | when grill in corner of hood
| 133132 | when grill in center of hood (centered on long axis -- can't fully center on short axis)
Balometer hood variation in flow (looking across hood opening along long rectangular axis)
Using rotating vane at cross section (fpm)
when grill in corner of hood
| 100 |  | 102
89
| 120 |  | 130-160 | depending on exact placement
when grill in center of hood
| 130 |  | 86
69
| 138 |  | 120
Balometer cfm goes up when obstruct 2/3 of grid with paper
| 46,47 | 60,61
| 75,77 | 90,92 | 101,99* | *adding additional paper to 7/8
Balometer grid has single pair of manometer readings
SUMMARY OF BALOMETER ISSUES -- IS VULNERABLE TO UNEVEN FLOW; UNEVEN FLOW INEVITABLE WITH SMALL GRIDS
Cannot control relative error by consistent placement
Flow pattern vary with angle of duct entry to grill
Cannot achieve consistent placement anyway due to obstructions
Not optimal instrument for total flow computation except as a contrast.

## Traverse West
West supply branch |  | 602.7867 | FPM | 267.9052 | CFM |  |  | Kitchen | 294 | FPM | 57.7268 | CFM
Hot wire was 663 | [7 empty] | Hot wire was 528.6
Pitot Traverse | [7 empty] | TEST035
Avg | 619 | [6 empty] | Avg | 286
Min | 315 | [6 empty] | Min | 198
Max | 860 | [6 empty] | Max | 378
TEST001 | [7 empty] | 90% of max | 340.2
Samples transcribed from Data App | [7 empty] | Count OK
Temp truly was 103 per anemometo
104 from Hobo |  | 103.64
Was set at 95.8 for Entered Temp
Pressure is proportional to density and square of velocity. | [8 empty] | Test 35
Estimated density is proportional to temperature at same pressure -- so probe error due to temp setting is only: | [6 empty] | 1.0144 |  | Entered Temp 106, Supply 43.8
Bar 406.8
Sample number = (col -1)*5 + row | [8 empty] | 1 | 2
Read outside is .00002 in h20, 0 cfm | [7 empty] | 1 | 262 | 344
Looking west -- fpm | [7 empty] | 2 | 198 | 319
| 1 | 2 | 3 | 4 | 5 |  |  | 3 | 230 | 251
5 | 504 | 429 | 696 | 791 | 742 | 632.4 |  | 4 | 324 | 264
4 | 668 | 555 | 762 | 802 | 860 | 729.4 |  | 5 | 378 | 245
3 | 559 | 511 | 627 | 750 | 835 | 656.4 |  | 6 | 364 | 249
2 | 439 | 369 | 540 | 692 | 828 | 573.6
1 | 381 | 315 | 499 | 612 | 704 | 502.2
| 510.2 | 435.8 | 624.8 | 729.4 | 793.8 | 618.8 |  | TEST036
TEST003 | [7 empty] | Avg | 308
Redo with correct temp now 109.4 | [7 empty] | Min | 205
Avg | 603 | [6 empty] | Max | 405
Min | 313 | [6 empty] | 90% of max | 364.5
Max | 898 | [6 empty] | Count OK
Looking west -- fpm
| 1 | 2 | 3 | 4 | 5
5 | 327 | 441 | 534 | 707 | 871 | 576
4 | 500 | 583 | 730 | 779 | 898 | 698 |  |  | Test 36
3 | 584 | 587 | 585 | 744 | 870 | 674 |  |  | Entered Temp 106, Supply 43.8
2 | 359 | 407 | 486 | 749 | 814 | 563
1 | 313 | 350 | 436 | 600 | 826 | 505 |  |  | 1 | 2
| 416.6 | 473.6 | 554.2 | 715.8 | 855.8 | 603.2 |  | 1 | 237 | 319
TEST 008 | [7 empty] | 2 | 230 | 397
Loooking west -- fpm 2/3, 8:55:51 to | [7 empty] | 3 | 242 | 360
Redo with set temp 105 -- real drifting up to |  |  |  |  | 109.4 |  |  | 4 | 313 | 301
Avg | 586 | [6 empty] | 5 | 378 | 312
Min | 248 | [6 empty] | 6 | 405 | 205
Max | 913
| 1 | 2 | 3 | 4 | 5
5 | 439 | 573 | 573 | 797 | 738 | 624 |  | TEST 037
4 | 537 | 681 | 704 | 792 | 913 | 725.4 |  | Avg | 277
3 | 404 | 500 | 565 | 741 | 808 | 603.6 |  | Min | 196
2 | 367 | 395 | 415 | 706 | 744 | 525.4 |  | Max | 398
1 | 248 | 280 | 394 | 654 | 691 | 453.4 |  | 90% of max | 358.2
| 399 | 485.8 | 530.2 | 738 | 778.8 | 586.36 |  | Count OK
TEST009
Repeat col 5 row 4, 9:02:53AM |  |  | 978 | avg of 10 samples from 921 to 1051
Test 37
Entered Temp 106, Supply 43.8
[9 empty] | 1 | 2
[8 empty] | 1 | 206 | 292
[8 empty] | 2 | 221 | 256
[8 empty] | 3 | 261 | 315
[8 empty] | 4 | 315 | 258
[8 empty] | 5 | 380 | 223
[8 empty] | 6 | 398 | 196
TEST 048
[8 empty] | Avg | 305
[8 empty] | Min | 252
[8 empty] | Max | 421
[8 empty] | 90% of max | 378.9
Count OK
Test 48
Entered Temp 106, Supply 41.9
[9 empty] | 1 | 2
[8 empty] | 1 | 263 | 302
[8 empty] | 2 | 258 | 300
[8 empty] | 3 | 252 | 255
[8 empty] | 4 | 336 | 285
[8 empty] | 5 | 407 | 303
[8 empty] | 6 | 421 | 280

## Traverse East
East supply branch 8 x10" |  |  | 423.16 | fpm | 235.0889 | cfm | 215.7282 | Check total | FAR East Branch (living room, hall only) 8x8" |  |  |  | 216.66 | fpm | 96.2222 | cfm | Dining Room -- 5" |  | 288.5 | fpm | Bed Room -- 5" |  | 214.5 | fpm | Gym -- 6" | 259.3333 | fpm
Hot wire was 453.6 | [8 empty] | No hot wire | [7 empty] | Hot wire was 338 |  | 39.3381 | cfm | No hot wire |  | 29.2479 | cfm | Hot wire was 288 |  |  | 50.92 | cfm
Pitot Traverse | [8 empty] | Pitot Traverse
Avg | 414 | [7 empty] | Avg | 218 | [6 empty] | Avg | 283 |  |  | Avg | 215 |  |  | Avg | 250
Min | 285 | [7 empty] | Min | 158 | [6 empty] | Min | 230 |  |  | Min | 183 |  |  | Min | 210
Max | 490 | [7 empty] | Max | 262 | [6 empty] | Max | 326 |  |  | Max | 257 |  |  | Max | 301
90% of max | 441 | [7 empty] | 90% of max | 235.8 | [6 empty] | 90% of max | 293.4 |  |  | 90% of max | 231.3 |  |  | 90% of max | 270.9
Count OK | 6 | [7 empty] | Count OK | 10 | [6 empty] | Count OK | 1 |  |  | Count OK | 2 |  |  | Count OK | 3
Samples transcribed from Data App | [8 empty] | Samples transcribed from Data App
Temp truly was rising to 110 per anemometer, |  |  |  |  | 109.4 | for hobo |  |  | TEST 025 | [12 empty] | test 030
TEST 014 | [16 empty] | Test 028
Test 32
Taken with supply temp entered a little low as 105 | [8 empty] | Taken with supply temp 42.61 |  |  | 108.698 | Anemometer 106.7 |  | Entered temp 106 |  |  | Entered Temp 106, Supply 41.45 |  |  |  | Entered Temp 106, Supply 41.6 |  |  |  | Entered Temp 106, Supply 43.8
NOTE: ON THIS TEST, THE PRESENCE OF ANEMOMETER PROBE MAY HAVE DISTORTED FLOW (ASCERTAINING HEAT)
Looking west -- FPM |  | 2/3,2:04:07, 2:14:04 |  |  | Test 14 |  |  |  | Looking west -- FPM |  | 2/4, 6:08:20 -6:14:54 |  |  | Test 25 |  |  |  | 1 | 2 |  |  | 1 | 2 |  |  | 1 | 2
| 1 | 2 | 3 | 4 | 5 |  |  |  |  | 1 | 2 | 3 | 4 | 5 |  |  | 1 | 235 | 295 |  | 1 | 186 | 205 |  | 1 | 248 | 240
5 | 382 | 430 | 442 | 445 | 403 | 420.4 |  |  | 5 | 210 | 207 | 242 | 232 | 187 | 215.6 |  | 2 | 290 | 230 |  | 2 | 217 | 231 |  | 2 | 259 | 288
4 | 384 | 457 | 431 | 463 | 434 | 433.8 |  |  | 4 | 241 | 248 | 249 | 262 | 246 | 249.2 |  | 3 | 290 | 296 |  | 3 | 206 | 223 |  | 3 | 277 | 301
3 | 389 | 433 | 430 | 411 | 420 | 416.6 |  |  | 3 | 242 | 251 | 246 | 259 | 223 | 244.2 |  | 4 | 319 | 253 |  | 4 | 244 | 204 |  | 4 | 245 | 258
2 | 438 | 490 | 445 | 435 | 402 | 442 |  |  | 2 | 228 | 195 | 217 | 227 | 172 | 207.8 |  | 5 | 326 | 284 |  | 5 | 257 | 200 |  | 5 | 249 | 210
1 | 285 | 379 | 324 | 380 | 421 | 357.8 |  |  | 1 | 158 | 182 | 201 | 171 | 162 | 174.8 |  | 6 | 282 | 296 |  | 6 | 218 | 183 |  | 6 | 216 | 214
| 375.6 | 437.8 | 414.4 | 426.8 | 416 | 414.12 |  |  |  | 215.8 | 216.6 | 231 | 230.2 | 198 | 218.32 | [11 empty] | -7 | extra reading out
TEST 015
Taken with entered temp mp now 110.8
Avg | 433 | [7 empty] | Pitot Traverse
Min | 339 | [7 empty] | Avg | 215 | [6 empty] | Avg | 294 |  |  | Avg | 214 |  |  | Avg | 259
Max | 498 | [7 empty] | Min | 156 | [6 empty] | Min | 238 |  |  | Min | 172 |  |  | Min | 230
90% of max | 448.2 | [7 empty] | Max | 258 | [6 empty] | Max | 338 |  |  | Max | 247 |  |  | Max | 294
COUNT ok | 8 | [7 empty] | 90% of max | 232.2 | [6 empty] | 90% of max | 304.2 |  |  | 90% of max | 222.3 |  |  | 90% of max | 264.6
Looking west -- FPM |  | 2/3. 2:16:42 to 2:21:50 |  |  | TEST 15 |  |  |  | Count OK | 10 | [6 empty] | Count OK | 8 |  |  | Count OK | 5 |  |  | Count OK | 4
| 1 | 2 | 3 | 4 | 5 |  |  |  | Samples transcribed from Data App
5 | 388 | 439 | 441 | 445 | 440 | 430.6 |  |  | Test 026
4 | 471 | 430 | 393 | 464 | 487 | 449 | [10 empty] | Test 029 |  |  |  |  | test 031
3 | 494 | 416 | 396 | 421 | 498 | 445 | [19 empty] | Test 33
2 | 478 | 421 | 426 | 415 | 480 | 444 |  |  | Taken with supply temp 42.61 |  |  | 108.698 | Anemometer 106.7 |  | Entered temp 106 |  |  | Entered Temp 106, Supply 41.45 |  |  |  | Entered Temp 106, Supply 41.6 |  |  |  | Entered Temp 106, Supply 43.8
1 | 339 | 412 | 389 | 400 | 431 | 394.2
| 434 | 423.6 | 409 | 429 | 467.2 | 432.56 |  |  | Looking west -- FPM |  | 2/4, 6:08:20 -6:14:54 |  |  | Test 26 |  |  |  | 1 | 2 |  |  | 1 | 2 |  |  | 1 | 2
TEST 019 | [9 empty] | 1 | 2 | 3 | 4 | 5 |  |  | 1 | 238 | 271 |  | 1 | 219 | 227 |  | 1 | 230 | 238
Taken with entered temp 106, supply temp was 41.4C or in F: | [5 empty] | 106.52 |  |  | 5 | 186 | 223 | 222 | 233 | 176 | 208 |  | 2 | 241 | 310 |  | 2 | 237 | 247 |  | 2 | 294 | 292
Avg | 423 | [7 empty] | 4 | 229 | 235 | 247 | 251 | 234 | 239.2 |  | 3 | 307 | 317 |  | 3 | 213 | 227 |  | 3 | 292 | 270
Min | 327 | [7 empty] | 3 | 224 | 241 | 258 | 237 | 248 | 241.6 |  | 4 | 319 | 296 |  | 4 | 223 | 209 |  | 4 | 244 | 243
Max | 477 | [7 empty] | 2 | 206 | 232 | 233 | 224 | 196 | 218.2 |  | 5 | 338 | 295 |  | 5 | 213 | 191 |  | 5 | 248 | 256
90% of max | 429.3 | [7 empty] | 1 | 156 | 173 | 163 | 190 | 158 | 168 |  | 6 | 318 | 278 |  | 6 | 172 | 195 |  | 6 | 252 | 242
COUNT ok | 14 | [8 empty] | 200.2 | 220.8 | 224.6 | 227 | 202.4 | 215
Looking west -- FPM |  | 2/4. 3:28:18 TO 3:34:05 |  |  | TEST 19 | [19 empty] | Avg | 269
| 1 | 2 | 3 | 4 | 5 | [19 empty] | Min | 234
5 | 425 | 467 | 467 | 452 | 440 | 450.2 | [18 empty] | Max | 308
4 | 426 | 430 | 419 | 396 | 456 | 425.4 | [18 empty] | 90% of max | 277.2
3 | 477 | 419 | 413 | 425 | 466 | 440 | [18 empty] | Count OK | 4
2 | 434 | 402 | 420 | 458 | 432 | 429.2
1 | 327 | 329 | 419 | 373 | 398 | 369.2
| 417.8 | 409.4 | 427.6 | 420.8 | 438.4 | 422.8
Test 34
Entered Temp 106, Supply 43.8
[26 empty] | 1 | 2
[25 empty] | 1 | 234 | 260
[25 empty] | 2 | 255 | 308
[25 empty] | 3 | 276 | 282
[25 empty] | 4 | 259 | 288
[25 empty] | 5 | 295 | 248
[25 empty] | 6 | 272 | 253

## Log Data
MODEL: | EBT731 |  | NOTE: Time entered is up to 1 minute behind.
SERIAL: | EBT731621014 |  | DATE IS ONE DAY AHEAD
TEST ID : | Test 001 | West supply branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 619 | 860 | 315 | ft/min | Actual Pitot
25 | 275.08 | 382.22 | 139.81 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
381 | 169.27 | 1 | 95.8 | 2024-02-04 | 06:53:54A
439 | 195.22 | 1 | 95.8 | 2024-02-04 | 06:54:04A
559 | 248.51 | 1 | 95.8 | 2024-02-04 | 06:54:15A
668 | 296.96 | 1 | 95.8 | 2024-02-04 | 06:54:27A
504 | 224 | 1 | 95.8 | 2024-02-04 | 06:54:45A
315 | 139.81 | 1 | 95.8 | 2024-02-04 | 06:55:45A
369 | 163.93 | 1 | 95.8 | 2024-02-04 | 06:55:55A
511 | 227.28 | 1 | 95.8 | 2024-02-04 | 06:56:06A
555 | 246.52 | 1 | 95.8 | 2024-02-04 | 06:56:17A
429 | 190.76 | 1 | 95.8 | 2024-02-04 | 06:56:27A
499 | 221.77 | 1 | 95.8 | 2024-02-04 | 06:57:25A
540 | 240.13 | 1 | 95.8 | 2024-02-04 | 06:57:40A
627 | 278.86 | 1 | 95.8 | 2024-02-04 | 06:57:53A
762 | 338.49 | 1 | 95.8 | 2024-02-04 | 06:58:08A
696 | 309.52 | 1 | 95.8 | 2024-02-04 | 06:58:20A
612 | 272.17 | 1 | 95.8 | 2024-02-04 | 06:59:09A
692 | 307.54 | 1 | 95.8 | 2024-02-04 | 06:59:18A
750 | 333.52 | 1 | 95.8 | 2024-02-04 | 06:59:28A
802 | 356.64 | 1 | 95.8 | 2024-02-04 | 06:59:38A
791 | 351.76 | 1 | 95.8 | 2024-02-04 | 06:59:50A
704 | 312.96 | 1 | 95.8 | 2024-02-04 | 07:00:33A
828 | 368.13 | 1 | 95.8 | 2024-02-04 | 07:00:45A
835 | 371.3 | 1 | 95.8 | 2024-02-04 | 07:00:56A
860 | 382.22 | 1 | 95.8 | 2024-02-04 | 07:01:10A
742 | 329.82 | 1 | 95.8 | 2024-02-04 | 07:01:29A
TEST ID : | Test 003 | West supply branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 603 | 898 | 313 | ft/min | Actual Pitot
25 | 268.12 | 399.26 | 139.22 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
313 | 139.22 | 1 | 109.4 | 2024-02-04 | 07:47:48A
359 | 159.58 | 1 | 109.4 | 2024-02-04 | 07:47:56A
584 | 259.51 | 1 | 109.4 | 2024-02-04 | 07:48:07A
500 | 222.28 | 1 | 109.4 | 2024-02-04 | 07:48:15A
327 | 145.21 | 1 | 109.4 | 2024-02-04 | 07:48:24A
350 | 155.59 | 1 | 109.4 | 2024-02-04 | 07:48:51A
407 | 180.96 | 1 | 109.4 | 2024-02-04 | 07:49:03A
587 | 260.93 | 1 | 109.4 | 2024-02-04 | 07:49:14A
583 | 259.06 | 1 | 109.4 | 2024-02-04 | 07:49:24A
441 | 196.21 | 1 | 109.4 | 2024-02-04 | 07:49:34A
436 | 193.74 | 1 | 109.4 | 2024-02-04 | 07:50:01A
486 | 216.05 | 1 | 109.4 | 2024-02-04 | 07:50:11A
585 | 260.08 | 1 | 109.4 | 2024-02-04 | 07:50:21A
730 | 324.48 | 1 | 109.4 | 2024-02-04 | 07:50:34A
534 | 237.33 | 1 | 109.4 | 2024-02-04 | 07:50:44A
600 | 266.45 | 1 | 109.4 | 2024-02-04 | 07:51:12A
749 | 332.96 | 1 | 109.4 | 2024-02-04 | 07:51:20A
744 | 330.51 | 1 | 109.4 | 2024-02-04 | 07:51:30A
779 | 346.19 | 1 | 109.4 | 2024-02-04 | 07:51:39A
707 | 314.25 | 1 | 109.4 | 2024-02-04 | 07:51:49A
826 | 367.25 | 1 | 109.4 | 2024-02-04 | 07:52:28A
814 | 361.99 | 1 | 109.4 | 2024-02-04 | 07:52:39A
870 | 386.64 | 1 | 109.4 | 2024-02-04 | 07:52:51A
898 | 399.26 | 1 | 109.4 | 2024-02-04 | 07:53:02A
871 | 387.16 | 1 | 109.4 | 2024-02-04 | 07:53:14A
SCRATCH TESTS
TEST ID : | Test 004
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
3 | -2e-05 | 0 | -4e-05 | in.H2O | Pressure
3 | 406.8 | 406.9 | 406.8 | in.H2O | Baro Press
3 | -7 | 0 | -20 | ft/min | Actual Pitot
3 | -3.04 | 0 | -9.11 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
-4e-05 | 406.8 | -20 | -9.11 | 1 | 109.4 | 2024-02-04 | 08:17:10A
-3e-05 | 406.9 | 0 | 0 | 1 | 109.4 | 2024-02-04 | 08:19:32A
0 | 406.8 | 0 | 0 | 1 | 109.4 | 2024-02-04 | 08:19:48A
TEST ID : | Test 005
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
11 | 0.01103 | 0.01821 | 0.00744 | in.H2O | Pressure
11 | 407.2 | 407.3 | 407.2 | in.H2O | Baro Press
11 | 431 | 560 | 355 | ft/min | Actual Pitot
11 | 191.47 | 248.91 | 157.6 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
0.01598 | 407.3 | 525 | 233.16 | 1 | 109.4 | 2024-02-04 | 08:47:37A
0.00998 | 407.2 | 415 | 184.34 | 1 | 109.4 | 2024-02-04 | 08:48:04A
0.01139 | 407.3 | 442 | 196.39 | 1 | 109.4 | 2024-02-04 | 08:48:12A
0.00744 | 407.3 | 355 | 157.6 | 1 | 109.4 | 2024-02-04 | 08:48:19A
0.01051 | 407.2 | 425 | 188.94 | 1 | 109.4 | 2024-02-04 | 08:48:26A
0.00774 | 407.2 | 365 | 162.42 | 1 | 109.4 | 2024-02-04 | 08:48:39A
0.00957 | 407.2 | 403 | 179.06 | 1 | 109.4 | 2024-02-04 | 08:48:46A
0.01134 | 407.3 | 440 | 195.57 | 1 | 109.4 | 2024-02-04 | 08:48:53A
0.00831 | 407.3 | 377 | 167.77 | 1 | 109.4 | 2024-02-04 | 08:49:22A
0.01083 | 407.2 | 432 | 191.96 | 1 | 109.4 | 2024-02-04 | 08:49:29A
0.01821 | 407.2 | 560 | 248.91 | 1 | 109.4 | 2024-02-04 | 08:49:42A
TEST ID : | Test 006
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
6 | 0.01672 | 0.01992 | 0.0149 | in.H2O | Pressure
6 | 407.3 | 407.3 | 407.2 | in.H2O | Baro Press
6 | 533 | 584 | 499 | ft/min | Actual Pitot
6 | 236.8 | 259.42 | 221.71 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
0.01617 | 407.3 | 517 | 229.83 | 1 | 109.4 | 2024-02-04 | 08:49:52A
0.01795 | 407.3 | 556 | 247.29 | 1 | 109.4 | 2024-02-04 | 08:50:02A
0.0149 | 407.3 | 499 | 221.71 | 1 | 109.4 | 2024-02-04 | 08:50:13A
0.01992 | 407.3 | 584 | 259.42 | 1 | 109.4 | 2024-02-04 | 08:50:20A
0.0155 | 407.2 | 517 | 229.81 | 1 | 109.4 | 2024-02-04 | 08:50:27A
0.0159 | 407.3 | 524 | 232.74 | 1 | 109.4 | 2024-02-04 | 08:50:34A
TEST ID : | Test 007
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
11 | 0.02272 | 0.02686 | 0.0191 | in.H2O | Pressure
11 | 407.2 | 407.3 | 407.2 | in.H2O | Baro Press
11 | 625 | 680 | 574 | ft/min | Actual Pitot
11 | 277.59 | 302.32 | 255.06 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
0.02637 | 407.3 | 674 | 299.66 | 1 | 109.4 | 2024-02-04 | 08:51:00A
0.0241 | 407.2 | 645 | 286.51 | 1 | 109.4 | 2024-02-04 | 08:51:09A
0.02023 | 407.2 | 589 | 261.9 | 1 | 109.4 | 2024-02-04 | 08:51:21A
0.0212 | 407.2 | 605 | 268.69 | 1 | 109.4 | 2024-02-04 | 08:51:29A
0.0191 | 407.3 | 574 | 255.06 | 1 | 109.4 | 2024-02-04 | 08:51:36A
0.0218 | 407.2 | 612 | 272.08 | 1 | 109.4 | 2024-02-04 | 08:51:44A
0.02239 | 407.3 | 621 | 276.17 | 1 | 109.4 | 2024-02-04 | 08:51:55A
0.02265 | 407.3 | 625 | 277.75 | 1 | 109.4 | 2024-02-04 | 08:52:06A
0.02686 | 407.3 | 680 | 302.32 | 1 | 109.4 | 2024-02-04 | 08:52:16A
0.0217 | 407.2 | 610 | 270.92 | 1 | 109.4 | 2024-02-04 | 08:52:23A
0.02347 | 407.3 | 635 | 282.4 | 1 | 109.4 | 2024-02-04 | 08:52:32A
TEST ID : | Test 008 | West supply branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 586 | 913 | 248 | ft/min | Actual Pitot
25 | 260.59 | 405.69 | 110.28 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
248 | 110.28 | 1 | 105.1 | 2024-02-04 | 08:55:51A
367 | 163.03 | 1 | 105.1 | 2024-02-04 | 08:55:59A
404 | 179.65 | 1 | 105.1 | 2024-02-04 | 08:56:09A
537 | 238.57 | 1 | 105.1 | 2024-02-04 | 08:56:19A
439 | 195.3 | 1 | 105.1 | 2024-02-04 | 08:56:26A
280 | 124.47 | 1 | 105.1 | 2024-02-04 | 08:56:46A
395 | 175.55 | 1 | 105.1 | 2024-02-04 | 08:56:54A
500 | 222.09 | 1 | 105.1 | 2024-02-04 | 08:57:01A
681 | 302.89 | 1 | 105.1 | 2024-02-04 | 08:57:09A
573 | 254.58 | 1 | 105.1 | 2024-02-04 | 08:57:17A
394 | 174.96 | 1 | 105.1 | 2024-02-04 | 08:57:43A
415 | 184.28 | 1 | 105.1 | 2024-02-04 | 08:57:50A
565 | 250.99 | 1 | 105.1 | 2024-02-04 | 08:58:21A
704 | 313.01 | 1 | 105.1 | 2024-02-04 | 08:58:28A
573 | 254.46 | 1 | 105.1 | 2024-02-04 | 08:58:36A
654 | 290.56 | 1 | 105.1 | 2024-02-04 | 08:59:11A
706 | 313.84 | 1 | 105.1 | 2024-02-04 | 08:59:20A
741 | 329.46 | 1 | 105.1 | 2024-02-04 | 08:59:31A
792 | 352.07 | 1 | 105.1 | 2024-02-04 | 08:59:39A
797 | 354.28 | 1 | 105.1 | 2024-02-04 | 08:59:49A
691 | 307.04 | 1 | 105.1 | 2024-02-04 | 09:00:54A
744 | 330.46 | 1 | 105.1 | 2024-02-04 | 09:01:07A
808 | 359.26 | 1 | 105.1 | 2024-02-04 | 09:01:20A
913 | 405.69 | 1 | 105.1 | 2024-02-04 | 09:01:32A
738 | 327.96 | 1 | 105.1 | 2024-02-04 | 09:01:43A
TEST ID : | Test 009 | West supply branch, col 5 row 4 -- repeat
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.05596 | 0.06456 | 0.04953 | in.H2O | Pressure
10 | 407.2 | 407.2 | 407.1 | in.H2O | Baro Press
10 | 978 | 1051 | 921 | ft/min | Actual Pitot
10 | 434.6 | 467.19 | 409.14 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
0.05466 | 407.1 | 966 | 429.54 | 1 | 105.1 | 2024-02-04 | 09:02:53A
0.04953 | 407.2 | 921 | 409.14 | 1 | 105.1 | 2024-02-04 | 09:03:04A
0.05869 | 407.2 | 1002 | 445.27 | 1 | 105.1 | 2024-02-04 | 09:03:17A
0.06456 | 407.1 | 1051 | 467.19 | 1 | 105.1 | 2024-02-04 | 09:03:29A
0.05517 | 407.1 | 971 | 431.45 | 1 | 105.1 | 2024-02-04 | 09:03:37A
0.05637 | 407.2 | 982 | 436.41 | 1 | 105.1 | 2024-02-04 | 09:03:49A
0.05402 | 407.2 | 962 | 427.38 | 1 | 105.1 | 2024-02-04 | 09:03:57A
0.05468 | 407.2 | 967 | 429.88 | 1 | 105.1 | 2024-02-04 | 09:04:07A
0.05602 | 407.2 | 979 | 435.1 | 1 | 105.1 | 2024-02-04 | 09:04:16A
0.05588 | 407.2 | 978 | 434.66 | 1 | 105.1 | 2024-02-04 | 09:04:26A
TEST ID : | Test 010 | external static pressure
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
18 | 0.38949 | 0.39579 | 0.38 | in.H2O | Pressure
18 | 406.2 | 406.2 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.38761 | 406.2 | 2024-02-04 | 01:46:39P
0.38592 | 406.2 | 2024-02-04 | 01:46:47P
0.3881 | 406.2 | 2024-02-04 | 01:46:57P
0.3869 | 406.1 | 2024-02-04 | 01:47:06P
0.38988 | 406.2 | 2024-02-04 | 01:47:14P
0.38956 | 406.2 | 2024-02-04 | 01:47:21P
0.3937 | 406.2 | 2024-02-04 | 01:47:30P
0.38686 | 406.2 | 2024-02-04 | 01:47:37P
0.39382 | 406.2 | 2024-02-04 | 01:47:44P
0.39417 | 406.2 | 2024-02-04 | 01:47:52P
0.39388 | 406.2 | 2024-02-04 | 01:48:03P
0.39379 | 406.2 | 2024-02-04 | 01:48:20P
0.39038 | 406.2 | 2024-02-04 | 01:48:31P
0.39579 | 406.2 | 2024-02-04 | 01:48:42P
0.38785 | 406.2 | 2024-02-04 | 01:48:49P
0.39107 | 406.2 | 2024-02-04 | 01:48:56P
0.38 | 406.1 | 2024-02-04 | 01:49:17P
0.38158 | 406.1 | 2024-02-04 | 01:49:28P
TEST ID : | Test 011 | external static pressure
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | 0.38873 | 0.39182 | 0.38458 | in.H2O | Pressure
5 | 406.1 | 406.2 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.3881 | 406.2 | 2024-02-04 | 01:49:49P
0.39055 | 406.1 | 2024-02-04 | 01:50:02P
0.38458 | 406.2 | 2024-02-04 | 01:50:12P
0.38859 | 406.1 | 2024-02-04 | 01:50:33P
0.39182 | 406.1 | 2024-02-04 | 01:50:40P
TEST ID : | Test 012 | external static pressure, out side filter
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.31384 | 0.31836 | 0.30154 | in.H2O | Pressure
10 | 406.2 | 406.3 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.31836 | 406.2 | 2024-02-04 | 01:51:44P
0.30154 | 406.2 | 2024-02-04 | 01:51:59P
0.31775 | 406.2 | 2024-02-04 | 01:52:09P
0.31484 | 406.2 | 2024-02-04 | 01:52:20P
0.31477 | 406.3 | 2024-02-04 | 01:52:30P
0.31217 | 406.3 | 2024-02-04 | 01:52:40P
0.31512 | 406.1 | 2024-02-04 | 01:52:48P
0.3147 | 406.2 | 2024-02-04 | 01:52:58P
0.31519 | 406.1 | 2024-02-04 | 01:53:08P
0.31398 | 406.1 | 2024-02-04 | 01:53:20P
TEST ID : | Test 013 | pressure in east main branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.03909 | 0.04355 | 0.03462 | in.H2O | Pressure
10 | 406.3 | 406.3 | 406.3 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.03742 | 406.3 | 2024-02-04 | 01:56:51P
0.04355 | 406.3 | 2024-02-04 | 01:57:07P
0.03773 | 406.3 | 2024-02-04 | 01:57:14P
0.03524 | 406.3 | 2024-02-04 | 01:57:21P
0.03875 | 406.3 | 2024-02-04 | 01:57:33P
0.04269 | 406.3 | 2024-02-04 | 01:57:41P
0.04132 | 406.3 | 2024-02-04 | 01:57:54P
0.03462 | 406.3 | 2024-02-04 | 01:58:05P
0.03638 | 406.3 | 2024-02-04 | 01:58:14P
0.04319 | 406.3 | 2024-02-04 | 01:58:27P
TEST ID : | Test 014 | East supply branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 414 | 490 | 285 | ft/min | Actual Pitot
25 | 230.12 | 272 | 158.16 | CFM | Actual Pitot \Rect X Size 10.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
285 | 158.16 | 1 | 105.1 | 2024-02-04 | 02:04:07P
438 | 243.48 | 1 | 105.1 | 2024-02-04 | 02:04:18P
389 | 215.93 | 1 | 105.1 | 2024-02-04 | 02:04:28P
384 | 213.53 | 1 | 105.1 | 2024-02-04 | 02:04:37P
382 | 212.22 | 1 | 105.1 | 2024-02-04 | 02:04:48P
379 | 210.65 | 1 | 105.1 | 2024-02-04 | 02:08:34P
490 | 272 | 1 | 105.1 | 2024-02-04 | 02:08:43P
433 | 240.65 | 1 | 105.1 | 2024-02-04 | 02:08:53P
457 | 254.02 | 1 | 105.1 | 2024-02-04 | 02:09:01P
430 | 238.98 | 1 | 105.1 | 2024-02-04 | 02:09:09P
324 | 180 | 1 | 105.1 | 2024-02-04 | 02:09:58P
445 | 247.33 | 1 | 105.1 | 2024-02-04 | 02:10:07P
430 | 239.04 | 1 | 105.1 | 2024-02-04 | 02:10:16P
431 | 239.22 | 1 | 105.1 | 2024-02-04 | 02:10:24P
442 | 245.56 | 1 | 105.1 | 2024-02-04 | 02:10:32P
380 | 211.32 | 1 | 105.1 | 2024-02-04 | 02:11:44P
435 | 241.86 | 1 | 105.1 | 2024-02-04 | 02:11:51P
411 | 228.29 | 1 | 105.1 | 2024-02-04 | 02:11:58P
463 | 257.3 | 1 | 105.1 | 2024-02-04 | 02:12:07P
445 | 247.49 | 1 | 105.1 | 2024-02-04 | 02:12:18P
421 | 234.06 | 1 | 105.1 | 2024-02-04 | 02:13:21P
402 | 223.4 | 1 | 105.1 | 2024-02-04 | 02:13:29P
420 | 233.2 | 1 | 105.1 | 2024-02-04 | 02:13:40P
434 | 241.2 | 1 | 105.1 | 2024-02-04 | 02:13:54P
403 | 224.03 | 1 | 105.1 | 2024-02-04 | 02:14:04P
TEST ID : | Test 015 | East supply branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 433 | 498 | 339 | ft/min | Actual Pitot
25 | 240.34 | 276.59 | 188.53 | CFM | Actual Pitot \Rect X Size 10.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
339 | 188.53 | 1 | 110.8 | 2024-02-04 | 02:16:42P
478 | 265.67 | 1 | 110.8 | 2024-02-04 | 02:16:51P
494 | 274.34 | 1 | 110.8 | 2024-02-04 | 02:16:58P
471 | 261.82 | 1 | 110.8 | 2024-02-04 | 02:17:07P
388 | 215.32 | 1 | 110.8 | 2024-02-04 | 02:17:16P
412 | 228.81 | 1 | 110.8 | 2024-02-04 | 02:17:47P
421 | 234.01 | 1 | 110.8 | 2024-02-04 | 02:17:54P
416 | 231.1 | 1 | 110.8 | 2024-02-04 | 02:18:01P
430 | 238.98 | 1 | 110.8 | 2024-02-04 | 02:18:09P
439 | 244.1 | 1 | 110.8 | 2024-02-04 | 02:18:17P
389 | 216.06 | 1 | 110.8 | 2024-02-04 | 02:18:46P
426 | 236.84 | 1 | 110.8 | 2024-02-04 | 02:18:56P
396 | 220.27 | 1 | 110.8 | 2024-02-04 | 02:19:05P
393 | 218.07 | 1 | 110.8 | 2024-02-04 | 02:19:15P
441 | 244.76 | 1 | 110.8 | 2024-02-04 | 02:19:24P
400 | 222.33 | 1 | 110.8 | 2024-02-04 | 02:19:58P
415 | 230.38 | 1 | 110.8 | 2024-02-04 | 02:20:07P
421 | 233.77 | 1 | 110.8 | 2024-02-04 | 02:20:16P
464 | 257.9 | 1 | 110.8 | 2024-02-04 | 02:20:26P
445 | 247.23 | 1 | 110.8 | 2024-02-04 | 02:20:35P
431 | 239.37 | 1 | 110.8 | 2024-02-04 | 02:21:15P
480 | 266.77 | 1 | 110.8 | 2024-02-04 | 02:21:24P
498 | 276.59 | 1 | 110.8 | 2024-02-04 | 02:21:33P
487 | 270.73 | 1 | 110.8 | 2024-02-04 | 02:21:43P
440 | 244.7 | 1 | 110.8 | 2024-02-04 | 02:21:50P
TEST ID : | Test 016 | scratch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
3 | 0.01006 | 0.01256 | 0.00834 | in.H2O | Pressure
3 | 406 | 406 | 405.9 | in.H2O | Baro Press
3 | 416 | 467 | 380 | ft/min | Actual Pitot
3 | 230.94 | 259.21 | 211.27 | CFM | Actual Pitot \Rect X Size 10.0 in Rect Y Size 8.0 in
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
0.00834 | 406 | 380 | 211.27 | 1 | 110.8 | 2024-02-04 | 03:10:39P
0.00927 | 406 | 400 | 222.35 | 1 | 110.8 | 2024-02-04 | 03:10:48P
0.01256 | 405.9 | 467 | 259.21 | 1 | 110.8 | 2024-02-04 | 03:10:58P
TEST ID : | Test 017 | DROPPED TUBE
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
17 | -215 | 0 | -775 | ft/min | Actual Pitot
17 | -119.44 | 0 | -430.31 | CFM | Actual Pitot \Rect X Size 10.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
-681 | -378.09 | 1 | 105 | 2024-02-04 | 03:16:08P
-696 | -386.77 | 1 | 105 | 2024-02-04 | 03:16:16P
-700 | -388.93 | 1 | 105 | 2024-02-04 | 03:16:26P
-696 | -386.46 | 1 | 105 | 2024-02-04 | 03:16:36P
-775 | -430.31 | 1 | 105 | 2024-02-04 | 03:16:43P
-26 | -14.71 | 1 | 105 | 2024-02-04 | 03:17:11P
-19 | -10.51 | 1 | 105 | 2024-02-04 | 03:17:25P
0 | 0 | 1 | 105 | 2024-02-04 | 03:17:39P
0 | 0 | 1 | 105 | 2024-02-04 | 03:18:00P
0 | 0 | 1 | 105 | 2024-02-04 | 03:18:15P
-20 | -11 | 1 | 105 | 2024-02-04 | 03:19:00P
-18 | -10.03 | 1 | 105 | 2024-02-04 | 03:19:13P
-8 | -4.51 | 1 | 105 | 2024-02-04 | 03:19:26P
0 | 0 | 1 | 105 | 2024-02-04 | 03:19:38P
0 | 0 | 1 | 105 | 2024-02-04 | 03:19:51P
-16 | -9.1 | 1 | 105 | 2024-02-04 | 03:20:33P
0 | 0 | 1 | 105 | 2024-02-04 | 03:20:51P
TEST ID : | Test 018 | DROPPED TUBE
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
2 | -711 | -711 | -712 | ft/min | Actual Pitot
2 | -395.28 | -394.89 | -395.66 | CFM | Actual Pitot \Rect X Size 10.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
-712 | -395.66 | 1 | 106 | 2024-02-04 | 03:26:29P
-711 | -394.89 | 1 | 106 | 2024-02-04 | 03:26:43P
TEST ID : | Test 019 | East supply branch
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 423 | 477 | 327 | ft/min | Actual Pitot
25 | 234.82 | 264.91 | 181.52 | CFM | Actual Pitot \Rect X Size 10.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
327 | 181.52 | 1 | 106 | 2024-02-04 | 03:28:18P
434 | 241.21 | 1 | 106 | 2024-02-04 | 03:28:25P
477 | 264.91 | 1 | 106 | 2024-02-04 | 03:28:33P
426 | 236.52 | 1 | 106 | 2024-02-04 | 03:28:42P
425 | 236.06 | 1 | 106 | 2024-02-04 | 03:28:52P
329 | 183.03 | 1 | 106 | 2024-02-04 | 03:29:25P
402 | 223.22 | 1 | 106 | 2024-02-04 | 03:29:38P
419 | 232.77 | 1 | 106 | 2024-02-04 | 03:29:46P
430 | 238.88 | 1 | 106 | 2024-02-04 | 03:29:55P
467 | 259.34 | 1 | 106 | 2024-02-04 | 03:30:02P
419 | 232.51 | 1 | 106 | 2024-02-04 | 03:31:10P
420 | 233.36 | 1 | 106 | 2024-02-04 | 03:31:17P
413 | 229.41 | 1 | 106 | 2024-02-04 | 03:31:25P
419 | 232.62 | 1 | 106 | 2024-02-04 | 03:31:33P
467 | 259.27 | 1 | 106 | 2024-02-04 | 03:31:42P
373 | 207.11 | 1 | 106 | 2024-02-04 | 03:32:13P
458 | 254.27 | 1 | 106 | 2024-02-04 | 03:32:21P
425 | 236.15 | 1 | 106 | 2024-02-04 | 03:32:30P
396 | 219.85 | 1 | 106 | 2024-02-04 | 03:32:39P
452 | 251.1 | 1 | 106 | 2024-02-04 | 03:32:49P
398 | 220.84 | 1 | 106 | 2024-02-04 | 03:33:28P
432 | 239.9 | 1 | 106 | 2024-02-04 | 03:33:36P
466 | 258.78 | 1 | 106 | 2024-02-04 | 03:33:46P
456 | 253.2 | 1 | 106 | 2024-02-04 | 03:33:55P
440 | 244.67 | 1 | 106 | 2024-02-04 | 03:34:05P
TEST ID : | Test 020 | esp @ 38 watts
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
11 | 0.16984 | 0.17146 | 0.16653 | in.H2O | Pressure
11 | 406.5 | 406.6 | 406.5 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.16814 | 406.6 | 2024-02-05 | 05:50:40A
0.17049 | 406.5 | 2024-02-05 | 05:50:48A
0.17138 | 406.5 | 2024-02-05 | 05:50:59A
0.1712 | 406.5 | 2024-02-05 | 05:51:08A
0.16974 | 406.5 | 2024-02-05 | 05:51:24A
0.16834 | 406.6 | 2024-02-05 | 05:51:37A
0.17146 | 406.5 | 2024-02-05 | 05:51:47A
0.16653 | 406.6 | 2024-02-05 | 05:51:58A
0.17026 | 406.5 | 2024-02-05 | 05:52:09A
0.16953 | 406.5 | 2024-02-05 | 05:52:24A
0.1712 | 406.5 | 2024-02-05 | 05:52:42A
TEST ID : | Test 021 | esp @60 waats
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | 0.2683 | 0.27203 | 0.26543 | in.H2O | Pressure
5 | 406.5 | 406.5 | 406.4 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.26872 | 406.5 | 2024-02-05 | 05:53:00A
0.26773 | 406.4 | 2024-02-05 | 05:53:12A
0.27203 | 406.5 | 2024-02-05 | 05:53:22A
0.26761 | 406.5 | 2024-02-05 | 05:53:32A
0.26543 | 406.5 | 2024-02-05 | 05:53:43A
TEST ID : | Test 022 | esp@ 94 watts
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.39199 | 0.39754 | 0.38569 | in.H2O | Pressure
10 | 406.4 | 406.5 | 406.4 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.39475 | 406.4 | 2024-02-05 | 05:54:10A
0.38569 | 406.4 | 2024-02-05 | 05:54:21A
0.39269 | 406.4 | 2024-02-05 | 05:54:29A
0.39754 | 406.5 | 2024-02-05 | 05:54:36A
0.38675 | 406.4 | 2024-02-05 | 05:54:47A
0.39651 | 406.4 | 2024-02-05 | 05:54:58A
0.38745 | 406.5 | 2024-02-05 | 05:55:10A
0.39603 | 406.5 | 2024-02-05 | 05:55:25A
0.39291 | 406.5 | 2024-02-05 | 05:55:34A
0.38961 | 406.4 | 2024-02-05 | 05:55:50A
TEST ID : | Test 023 | just the supply
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | 0.16886 | 0.17501 | 0.15762 | in.H2O | Pressure
5 | 406.6 | 406.7 | 406.6 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.17501 | 406.7 | 2024-02-05 | 05:57:58A
0.17363 | 406.6 | 2024-02-05 | 05:58:13A
0.15762 | 406.7 | 2024-02-05 | 05:58:34A
0.17048 | 406.6 | 2024-02-05 | 05:59:38A
0.16755 | 406.6 | 2024-02-05 | 05:59:47A
TEST ID : | Test 024 | just the return
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
4 | 0.22057 | 0.22338 | 0.2179 | in.H2O | Pressure
4 | 406.4 | 406.4 | 406.3 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.21978 | 406.4 | 2024-02-05 | 06:02:06A
0.22338 | 406.4 | 2024-02-05 | 06:02:17A
0.22123 | 406.4 | 2024-02-05 | 06:02:26A
0.2179 | 406.3 | 2024-02-05 | 06:02:38A
TEST ID : | Test 025 | Far east traverse
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 218 | 262 | 158 | ft/min | Actual Pitot
25 | 97.04 | 116.65 | 70.32 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
158 | 70.32 | 1 | 106 | 2024-02-05 | 06:08:20A
228 | 101.49 | 1 | 106 | 2024-02-05 | 06:08:34A
242 | 107.7 | 1 | 106 | 2024-02-05 | 06:08:44A
241 | 107.32 | 1 | 106 | 2024-02-05 | 06:08:54A
210 | 93.19 | 1 | 106 | 2024-02-05 | 06:09:07A
182 | 80.98 | 1 | 106 | 2024-02-05 | 06:09:46A
195 | 86.72 | 1 | 106 | 2024-02-05 | 06:09:57A
251 | 111.72 | 1 | 106 | 2024-02-05 | 06:10:06A
248 | 110.34 | 1 | 106 | 2024-02-05 | 06:10:22A
207 | 92.04 | 1 | 106 | 2024-02-05 | 06:10:32A
201 | 89.18 | 1 | 106 | 2024-02-05 | 06:11:02A
217 | 96.63 | 1 | 106 | 2024-02-05 | 06:11:11A
246 | 109.55 | 1 | 106 | 2024-02-05 | 06:11:21A
249 | 110.47 | 1 | 106 | 2024-02-05 | 06:11:31A
242 | 107.34 | 1 | 106 | 2024-02-05 | 06:11:41A
171 | 75.96 | 1 | 106 | 2024-02-05 | 06:12:13A
227 | 100.95 | 1 | 106 | 2024-02-05 | 06:12:24A
259 | 114.89 | 1 | 106 | 2024-02-05 | 06:12:35A
262 | 116.65 | 1 | 106 | 2024-02-05 | 06:12:43A
232 | 103.12 | 1 | 106 | 2024-02-05 | 06:13:40A
162 | 72.09 | 1 | 106 | 2024-02-05 | 06:14:06A
172 | 76.23 | 1 | 106 | 2024-02-05 | 06:14:20A
223 | 98.96 | 1 | 106 | 2024-02-05 | 06:14:32A
246 | 109.14 | 1 | 106 | 2024-02-05 | 06:14:41A
187 | 83 | 1 | 106 | 2024-02-05 | 06:14:54A
TEST ID : | Test 026 | Far east traverse
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
25 | 215 | 258 | 156 | ft/min | Actual Pitot
25 | 95.58 | 114.54 | 69.28 | CFM | Actual Pitot \Rect X Size 8.0 in Rect Y Size 8.0 in
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
156 | 69.28 | 1 | 106 | 2024-02-05 | 06:15:36A
206 | 91.65 | 1 | 106 | 2024-02-05 | 06:15:46A
224 | 99.62 | 1 | 106 | 2024-02-05 | 06:15:57A
229 | 101.98 | 1 | 106 | 2024-02-05 | 06:16:08A
186 | 82.63 | 1 | 106 | 2024-02-05 | 06:16:20A
173 | 76.77 | 1 | 106 | 2024-02-05 | 06:16:47A
232 | 103.28 | 1 | 106 | 2024-02-05 | 06:16:58A
241 | 107.03 | 1 | 106 | 2024-02-05 | 06:17:10A
235 | 104.53 | 1 | 106 | 2024-02-05 | 06:17:21A
223 | 99.03 | 1 | 106 | 2024-02-05 | 06:17:33A
163 | 72.44 | 1 | 106 | 2024-02-05 | 06:18:02A
233 | 103.77 | 1 | 106 | 2024-02-05 | 06:18:12A
258 | 114.54 | 1 | 106 | 2024-02-05 | 06:18:20A
247 | 109.88 | 1 | 106 | 2024-02-05 | 06:18:30A
222 | 98.86 | 1 | 106 | 2024-02-05 | 06:18:41A
190 | 84.39 | 1 | 106 | 2024-02-05 | 06:19:08A
224 | 99.56 | 1 | 106 | 2024-02-05 | 06:19:18A
237 | 105.25 | 1 | 106 | 2024-02-05 | 06:19:29A
251 | 111.48 | 1 | 106 | 2024-02-05 | 06:19:39A
233 | 103.62 | 1 | 106 | 2024-02-05 | 06:19:50A
158 | 70.03 | 1 | 106 | 2024-02-05 | 06:20:25A
196 | 87.25 | 1 | 106 | 2024-02-05 | 06:20:38A
248 | 110.33 | 1 | 106 | 2024-02-05 | 06:20:47A
234 | 103.99 | 1 | 106 | 2024-02-05 | 06:20:58A
176 | 78.43 | 1 | 106 | 2024-02-05 | 06:21:12A
TEST ID : | Test 027 | scrub
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | 318 | 357 | 243 | ft/min | Actual Pitot
5 | 43.34 | 48.66 | 33.15 | CFM | Actual Pitot \Round Duct 5.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
243 | 33.15 | 1 | 106 | 2024-02-05 | 07:14:56A
309 | 42.15 | 1 | 106 | 2024-02-05 | 07:15:08A
346 | 47.22 | 1 | 106 | 2024-02-05 | 07:15:18A
334 | 45.48 | 1 | 106 | 2024-02-05 | 07:15:26A
357 | 48.66 | 1 | 106 | 2024-02-05 | 07:15:44A
TEST ID : | Test 028 | Dining Room
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 283 | 326 | 230 | ft/min | Actual Pitot
12 | 38.58 | 44.46 | 31.42 | CFM | Actual Pitot \Round Duct 5.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
235 | 32.02 | 1 | 106 | 2024-02-05 | 07:17:22A
290 | 39.52 | 1 | 106 | 2024-02-05 | 07:17:38A
290 | 39.5 | 1 | 106 | 2024-02-05 | 07:17:48A
319 | 43.46 | 1 | 106 | 2024-02-05 | 07:18:03A
326 | 44.46 | 1 | 106 | 2024-02-05 | 07:18:43A
282 | 38.52 | 1 | 106 | 2024-02-05 | 07:20:02A
295 | 40.17 | 1 | 106 | 2024-02-05 | 07:20:28A
230 | 31.42 | 1 | 106 | 2024-02-05 | 07:20:42A
296 | 40.32 | 1 | 106 | 2024-02-05 | 07:20:49A
253 | 34.48 | 1 | 106 | 2024-02-05 | 07:21:03A
284 | 38.77 | 1 | 106 | 2024-02-05 | 07:21:14A
296 | 40.31 | 1 | 106 | 2024-02-05 | 07:21:27A
TEST ID : | Test 029 | Dining Room
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 294 | 338 | 238 | ft/min | Actual Pitot
12 | 40.09 | 46.13 | 32.39 | CFM | Actual Pitot \Round Duct 5.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
238 | 32.39 | 1 | 106 | 2024-02-05 | 07:22:20A
241 | 32.91 | 1 | 106 | 2024-02-05 | 07:22:30A
307 | 41.88 | 1 | 106 | 2024-02-05 | 07:22:40A
319 | 43.51 | 1 | 106 | 2024-02-05 | 07:22:48A
338 | 46.13 | 1 | 106 | 2024-02-05 | 07:22:58A
318 | 43.34 | 1 | 106 | 2024-02-05 | 07:23:11A
271 | 36.93 | 1 | 106 | 2024-02-05 | 07:23:42A
310 | 42.25 | 1 | 106 | 2024-02-05 | 07:23:50A
317 | 43.26 | 1 | 106 | 2024-02-05 | 07:23:58A
296 | 40.41 | 1 | 106 | 2024-02-05 | 07:24:15A
295 | 40.25 | 1 | 106 | 2024-02-05 | 07:24:24A
278 | 37.87 | 1 | 106 | 2024-02-05 | 07:24:40A
TEST ID : | Test 030 | Bed room
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 215 | 257 | 183 | ft/min | Actual Pitot
12 | 29.25 | 35.05 | 24.96 | CFM | Actual Pitot \Round Duct 5.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
186 | 25.32 | 1 | 106 | 2024-02-05 | 07:27:33A
217 | 29.64 | 1 | 106 | 2024-02-05 | 07:27:42A
206 | 28.02 | 1 | 106 | 2024-02-05 | 07:27:52A
244 | 33.3 | 1 | 106 | 2024-02-05 | 07:28:03A
257 | 35.05 | 1 | 106 | 2024-02-05 | 07:28:12A
218 | 29.74 | 1 | 106 | 2024-02-05 | 07:28:25A
205 | 27.99 | 1 | 106 | 2024-02-05 | 07:28:57A
231 | 31.55 | 1 | 106 | 2024-02-05 | 07:29:10A
223 | 30.44 | 1 | 106 | 2024-02-05 | 07:29:18A
204 | 27.77 | 1 | 106 | 2024-02-05 | 07:29:27A
200 | 27.23 | 1 | 106 | 2024-02-05 | 07:29:36A
183 | 24.96 | 1 | 106 | 2024-02-05 | 07:29:47A
TEST ID : | Test 031 | Bed room
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 214 | 247 | 172 | ft/min | Actual Pitot
12 | 29.24 | 33.65 | 23.45 | CFM | Actual Pitot \Round Duct 5.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
219 | 29.8 | 1 | 106 | 2024-02-05 | 07:30:21A
237 | 32.35 | 1 | 106 | 2024-02-05 | 07:30:36A
213 | 29.07 | 1 | 106 | 2024-02-05 | 07:30:49A
223 | 30.34 | 1 | 106 | 2024-02-05 | 07:30:58A
213 | 29.11 | 1 | 106 | 2024-02-05 | 07:31:13A
172 | 23.45 | 1 | 106 | 2024-02-05 | 07:31:27A
227 | 30.99 | 1 | 106 | 2024-02-05 | 07:31:54A
247 | 33.65 | 1 | 106 | 2024-02-05 | 07:32:02A
227 | 30.92 | 1 | 106 | 2024-02-05 | 07:32:11A
209 | 28.55 | 1 | 106 | 2024-02-05 | 07:32:22A
191 | 26.01 | 1 | 106 | 2024-02-05 | 07:32:37A
195 | 26.59 | 1 | 106 | 2024-02-05 | 07:32:50A
TEST ID : | Test 032 | Gym
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
13 | 230 | 301 | -7 | ft/min | Actual Pitot
13 | 45.25 | 59.06 | -1.42 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
248 | 48.64 | 1 | 106 | 2024-02-05 | 08:13:06A
259 | 50.89 | 1 | 106 | 2024-02-05 | 08:13:15A
277 | 54.37 | 1 | 106 | 2024-02-05 | 08:13:30A
245 | 48.04 | 1 | 106 | 2024-02-05 | 08:13:40A
249 | 48.87 | 1 | 106 | 2024-02-05 | 08:13:49A
216 | 42.41 | 1 | 106 | 2024-02-05 | 08:14:01A
240 | 47.06 | 1 | 106 | 2024-02-05 | 08:14:41A
288 | 56.55 | 1 | 106 | 2024-02-05 | 08:14:49A
301 | 59.06 | 1 | 106 | 2024-02-05 | 08:14:57A
258 | 50.56 | 1 | 106 | 2024-02-05 | 08:15:05A
210 | 41.21 | 1 | 106 | 2024-02-05 | 08:15:14A
214 | 42.01 | 1 | 106 | 2024-02-05 | 08:15:26A
-7 | -1.42 | 1 | 106 | 2024-02-05 | 08:15:47A
TEST ID : | Test 033 | Gym
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 259 | 294 | 230 | ft/min | Actual Pitot
12 | 50.77 | 57.67 | 45.14 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
230 | 45.14 | 1 | 106 | 2024-02-05 | 08:16:19A
294 | 57.67 | 1 | 106 | 2024-02-05 | 08:16:30A
292 | 57.41 | 1 | 106 | 2024-02-05 | 08:16:38A
244 | 47.91 | 1 | 106 | 2024-02-05 | 08:16:48A
248 | 48.79 | 1 | 106 | 2024-02-05 | 08:16:55A
252 | 49.55 | 1 | 106 | 2024-02-05 | 08:17:04A
238 | 46.82 | 1 | 106 | 2024-02-05 | 08:17:36A
292 | 57.37 | 1 | 106 | 2024-02-05 | 08:17:42A
270 | 53.05 | 1 | 106 | 2024-02-05 | 08:17:51A
243 | 47.66 | 1 | 106 | 2024-02-05 | 08:17:58A
256 | 50.34 | 1 | 106 | 2024-02-05 | 08:18:06A
242 | 47.58 | 1 | 106 | 2024-02-05 | 08:18:16A
TEST ID : | Test 034 | Gym
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 269 | 308 | 234 | ft/min | Actual Pitot
12 | 52.83 | 60.42 | 46.04 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
234 | 46.04 | 1 | 106 | 2024-02-05 | 08:19:41A
255 | 50.09 | 1 | 106 | 2024-02-05 | 08:19:50A
276 | 54.18 | 1 | 106 | 2024-02-05 | 08:19:57A
259 | 50.79 | 1 | 106 | 2024-02-05 | 08:20:04A
295 | 57.91 | 1 | 106 | 2024-02-05 | 08:20:13A
272 | 53.34 | 1 | 106 | 2024-02-05 | 08:20:23A
260 | 51.07 | 1 | 106 | 2024-02-05 | 08:20:53A
308 | 60.42 | 1 | 106 | 2024-02-05 | 08:21:03A
282 | 55.31 | 1 | 106 | 2024-02-05 | 08:21:12A
288 | 56.61 | 1 | 106 | 2024-02-05 | 08:21:22A
248 | 48.61 | 1 | 106 | 2024-02-05 | 08:21:29A
253 | 49.63 | 1 | 106 | 2024-02-05 | 08:21:37A
TEST ID : | Test 035 | Kitchen
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 286 | 378 | 198 | ft/min | Actual Pitot
12 | 56.09 | 74.25 | 38.94 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
262 | 51.52 | 1 | 106 | 2024-02-05 | 08:24:22A
198 | 38.94 | 1 | 106 | 2024-02-05 | 08:24:33A
230 | 45.08 | 1 | 106 | 2024-02-05 | 08:24:45A
324 | 63.54 | 1 | 106 | 2024-02-05 | 08:24:53A
378 | 74.25 | 1 | 106 | 2024-02-05 | 08:25:00A
364 | 71.55 | 1 | 106 | 2024-02-05 | 08:25:11A
344 | 67.48 | 1 | 106 | 2024-02-05 | 08:25:41A
319 | 62.61 | 1 | 106 | 2024-02-05 | 08:25:49A
251 | 49.28 | 1 | 106 | 2024-02-05 | 08:26:13A
264 | 51.76 | 1 | 106 | 2024-02-05 | 08:26:35A
245 | 48.07 | 1 | 106 | 2024-02-05 | 08:26:58A
249 | 48.96 | 1 | 106 | 2024-02-05 | 08:27:09A
TEST ID : | Test 036 | Kitchen
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 308 | 405 | 205 | ft/min | Actual Pitot
12 | 60.53 | 79.61 | 40.3 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
237 | 46.56 | 1 | 106 | 2024-02-05 | 08:27:53A
230 | 45.17 | 1 | 106 | 2024-02-05 | 08:28:05A
242 | 47.42 | 1 | 106 | 2024-02-05 | 08:28:16A
313 | 61.55 | 1 | 106 | 2024-02-05 | 08:28:26A
378 | 74.2 | 1 | 106 | 2024-02-05 | 08:28:41A
405 | 79.61 | 1 | 106 | 2024-02-05 | 08:29:27A
319 | 62.63 | 1 | 106 | 2024-02-05 | 08:29:47A
397 | 77.85 | 1 | 106 | 2024-02-05 | 08:29:57A
360 | 70.67 | 1 | 106 | 2024-02-05 | 08:30:04A
301 | 59.05 | 1 | 106 | 2024-02-05 | 08:30:11A
312 | 61.3 | 1 | 106 | 2024-02-05 | 08:30:24A
205 | 40.3 | 1 | 106 | 2024-02-05 | 08:30:36A
TEST ID : | Test 037 | Kitchen
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 277 | 398 | 196 | ft/min | Actual Pitot
12 | 54.32 | 78.07 | 38.45 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
206 | 40.47 | 1 | 106 | 2024-02-05 | 08:31:14A
221 | 43.35 | 1 | 106 | 2024-02-05 | 08:31:24A
261 | 51.16 | 1 | 106 | 2024-02-05 | 08:31:32A
315 | 61.76 | 1 | 106 | 2024-02-05 | 08:31:40A
380 | 74.63 | 1 | 106 | 2024-02-05 | 08:31:48A
398 | 78.07 | 1 | 106 | 2024-02-05 | 08:31:56A
292 | 57.35 | 1 | 106 | 2024-02-05 | 08:32:17A
256 | 50.18 | 1 | 106 | 2024-02-05 | 08:32:32A
315 | 61.88 | 1 | 106 | 2024-02-05 | 08:32:40A
258 | 50.67 | 1 | 106 | 2024-02-05 | 08:32:51A
223 | 43.87 | 1 | 106 | 2024-02-05 | 08:33:03A
196 | 38.45 | 1 | 106 | 2024-02-05 | 08:33:22A
TEST ID : | Test 038 | scrub
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
1 | 0.01672 | 0.01672 | 0.01672 | in.H2O | Pressure
1 | 406.3 | 406.3 | 406.3 | in.H2O | Baro Press
1 | 535 | 535 | 535 | ft/min | Actual Pitot
1 | 105.13 | 105.13 | 105.13 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Pressure | Baro Press | Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
0.01672 | 406.3 | 535 | 105.13 | 1 | 106 | 2024-02-05 | 08:46:22A
ERV ON Off Experiements
TEST ID : | Test 039
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | 0.00012 | 0.00013 | 9e-05 | in.H2O | Pressure
5 | 406.1 | 406.2 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.00013 | 406.2 | 2024-02-05 | 09:33:12A
0.00013 | 406.2 | 2024-02-05 | 09:33:25A
9e-05 | 406.1 | 2024-02-05 | 09:33:47A
0.00012 | 406.2 | 2024-02-05 | 09:34:07A
0.00013 | 406.1 | 2024-02-05 | 09:34:26A
TEST ID : | Test 040
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
6 | 8e-05 | 0.00014 | -7e-05 | in.H2O | Pressure
6 | 406.1 | 406.2 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.00014 | 406.2 | 2024-02-05 | 09:35:07A
0.00013 | 406.1 | 2024-02-05 | 09:35:20A
9e-05 | 406.1 | 2024-02-05 | 09:35:33A
9e-05 | 406.1 | 2024-02-05 | 09:35:49A
0.00011 | 406.1 | 2024-02-05 | 09:36:07A
-7e-05 | 406.2 | 2024-02-05 | 09:46:50A
TEST ID : | Test 041
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | -6e-05 | -4e-05 | -9e-05 | in.H2O | Pressure
5 | 406.2 | 406.3 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
-6e-05 | 406.2 | 2024-02-05 | 09:48:00A
-4e-05 | 406.3 | 2024-02-05 | 09:48:13A
-5e-05 | 406.2 | 2024-02-05 | 09:48:28A
-9e-05 | 406.1 | 2024-02-05 | 09:48:43A
-4e-05 | 406.2 | 2024-02-05 | 09:48:58A
TEST ID : | Test 042
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
5 | -4e-05 | -1e-05 | -7e-05 | in.H2O | Pressure
5 | 406.2 | 406.3 | 406.1 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
-6e-05 | 406.2 | 2024-02-05 | 09:49:37A
-7e-05 | 406.3 | 2024-02-05 | 09:49:49A
-1e-05 | 406.3 | 2024-02-05 | 09:50:08A
-3e-05 | 406.1 | 2024-02-05 | 09:50:26A
-1e-05 | 406.2 | 2024-02-05 | 09:50:45A
TEST ID : | Test 043
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.38346 | 0.39419 | 0.3749 | in.H2O | Pressure
10 | 406 | 406 | 405.9 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.39419 | 405.9 | 2024-02-05 | 09:56:48A
0.38512 | 406 | 2024-02-05 | 09:57:04A
0.37924 | 406 | 2024-02-05 | 09:57:13A
0.38521 | 406 | 2024-02-05 | 09:57:22A
0.38018 | 406 | 2024-02-05 | 09:57:32A
0.38472 | 406 | 2024-02-05 | 09:57:39A
0.38265 | 406 | 2024-02-05 | 09:57:51A
0.3749 | 406 | 2024-02-05 | 09:58:02A
0.38327 | 405.9 | 2024-02-05 | 09:58:12A
0.38511 | 406 | 2024-02-05 | 09:58:24A
TEST ID : | Test 044
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.38072 | 0.3855 | 0.37487 | in.H2O | Pressure
10 | 406 | 406 | 405.9 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.38504 | 405.9 | 2024-02-05 | 09:59:01A
0.37947 | 405.9 | 2024-02-05 | 09:59:11A
0.38493 | 406 | 2024-02-05 | 09:59:23A
0.3855 | 406 | 2024-02-05 | 09:59:33A
0.3777 | 405.9 | 2024-02-05 | 09:59:50A
0.37487 | 406 | 2024-02-05 | 10:00:00A
0.38237 | 405.9 | 2024-02-05 | 10:00:07A
0.38137 | 406 | 2024-02-05 | 10:00:14A
0.38021 | 406 | 2024-02-05 | 10:00:21A
0.37577 | 405.9 | 2024-02-05 | 10:00:28A
TEST ID : | Test 045
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.38375 | 0.38808 | 0.37589 | in.H2O | Pressure
10 | 405.9 | 406 | 405.8 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.38519 | 405.9 | 2024-02-05 | 10:05:36A
0.3849 | 405.9 | 2024-02-05 | 10:05:44A
0.38808 | 405.8 | 2024-02-05 | 10:05:56A
0.38367 | 405.9 | 2024-02-05 | 10:06:07A
0.38622 | 405.9 | 2024-02-05 | 10:06:14A
0.38474 | 406 | 2024-02-05 | 10:06:22A
0.37589 | 405.9 | 2024-02-05 | 10:06:29A
0.37955 | 405.9 | 2024-02-05 | 10:06:36A
0.38207 | 405.9 | 2024-02-05 | 10:06:44A
0.38719 | 406 | 2024-02-05 | 10:06:55A
TEST ID : | Test 046
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
10 | 0.37989 | 0.38598 | 0.3734 | in.H2O | Pressure
10 | 405.9 | 405.9 | 405.8 | in.H2O | Baro Press
DATA
Pressure | Baro Press | Date | Time
0.3839 | 405.9 | 2024-02-05 | 10:07:39A
0.37606 | 405.8 | 2024-02-05 | 10:07:46A
0.38576 | 405.9 | 2024-02-05 | 10:07:53A
0.37413 | 405.9 | 2024-02-05 | 10:08:02A
0.37905 | 405.9 | 2024-02-05 | 10:08:14A
0.38598 | 405.9 | 2024-02-05 | 10:08:22A
0.3734 | 405.9 | 2024-02-05 | 10:08:32A
0.37693 | 405.8 | 2024-02-05 | 10:08:43A
0.3787 | 405.9 | 2024-02-05 | 10:08:53A
0.38497 | 405.9 | 2024-02-05 | 10:09:01A
TEST ID : | Test 047 | scrub
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
2 | 263 | 271 | 254 | ft/min | Actual Pitot
2 | 51.56 | 53.24 | 49.88 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
271 | 53.24 | 1 | 106 | 2024-02-05 | 10:59:59A
254 | 49.88 | 1 | 106 | 2024-02-05 | 11:00:06A
TEST ID : | Test 048 | Kitchen
STATISTICS
# SAMPLES | Avg | Max | Min | UNIT | READING TYPE\ FLOW SIZE
12 | 305 | 421 | 252 | ft/min | Actual Pitot
12 | 59.92 | 82.62 | 49.4 | CFM | Actual Pitot \Round Duct 6.0 in dia
DATA
Actual Velocity (Pitot) | Actual Flow (Pitot) | Cf | Entered Temp | Date | Time
263 | 51.67 | 1 | 106 | 2024-02-05 | 11:00:41A
258 | 50.69 | 1 | 106 | 2024-02-05 | 11:00:48A
252 | 49.4 | 1 | 106 | 2024-02-05 | 11:00:55A
336 | 65.96 | 1 | 106 | 2024-02-05 | 11:01:03A
407 | 79.89 | 1 | 106 | 2024-02-05 | 11:01:13A
421 | 82.62 | 1 | 106 | 2024-02-05 | 11:01:25A
302 | 59.22 | 1 | 106 | 2024-02-05 | 11:01:49A
300 | 58.96 | 1 | 106 | 2024-02-05 | 11:01:57A
255 | 50.1 | 1 | 106 | 2024-02-05 | 11:02:07A
285 | 55.91 | 1 | 106 | 2024-02-05 | 11:02:17A
303 | 59.58 | 1 | 106 | 2024-02-05 | 11:02:25A
280 | 54.99 | 1 | 106 | 2024-02-05 | 11:02:36A

## ERV On off
ERV On off -- pressure comparison
tests 039 to 046
Nothing detectable at 0.1 inch level in barometer display
Place single pressure probe in living return vent -- 5 samples
ERV off | 0.00011 | 9e-05 | 0.00014
ERV on | 0.00012 | 9e-05 | 0.00013
Not significant difference -- hard to expect one, same room, no barrier
Place pressure probes for external static pressure (inside filter) -- 5 samples
ERV off | -4e-05 | -7e-05 | -1e-05
ERV on | -6e-05 | -9e-05 | -4e-05
Not significant difference, separated by air handler cabinet; not tightly sealed outside
Place pressure probes for external static pressure (inside filter) -- 5 samples
Run system full
ERV off | 0.38346 | 0.3749 | 0.39419 | test 043
ERV on | 0.38072 | 0.37487 | 0.3855
ERV off | 0.38375 | 0.37589 | 0.38808
ERV on | 0.37989 | 0.3734 | 0.38598
Avg off | 0.3836
Avg on | 0.38031
Possible difference if any is << .01"
NOTE prior hypothesis was greater flow when on (this would be opposite . . .)
Dispel this thought.

## Supply Duct Pressure
Duct Pressure Probe | Misc # of samples, averages |  | External Static Pressure -- probe in supply plenum; probe interior of filter (return); probe exterior to filter (return)
In west supply branch | 0.067 |  | Interior to the filter | single | avg | min | max
In air | 0.0002 |  | Start up 38 | 0.163
In DR Vent | 0.0065 |  | Start up 60 | 0.272
In east main branch | 0.03909 | test 013, 10 samples | Full blast 94 sample of 18 |  | 0.38949 | 0.38 | 0.39579 | test 010
In Basement ceiling grill | 0.016 |  | Full blast 94 sample of 5 more |  | 0.38873 | 0.38458 | 0.39182 | test 011 | (making sure supply probe straight)
In study return grill | -0.159 |  | Outside filter sample of 10 |  | 0.31384 | 0.30154 | 0.31836 | test 012
In gym vent | 0.0243
Kitchen vent | 0.135 |  | Interior to the filter | Count | avg | min | max
|  |  | Start up 38 | 11 | 0.16984 | 0.16653 | 0.17146 | test 20
|  |  | Start up 60 | 5 | 0.2683 | 0.26543 | 0.27203 | test 21
|  |  | Full Blast 95 | 10 | 0.39199 | 0.38569 | 0.39754 | test 22
|  |  | JUST THE SUPPLY | 5 | 0.16886 | 0.15762 | 0.17501 | test 23
|  |  | JUST THE RETURN | 4 | 0.22057 | 0.2179 | 0.22338 | test 24
https://www.energystar.gov/sites/default/files/specs/National%20Comfort%20Institute%20-%20Measure%20and%20Interpret%20Static%20Pressures.pdf
|  |  | So pressure downgrade at 38 |  | 0.43328 | 0.65824
|  |  | pressure downgrade at 60 |  | 0.68446 | 0.82732
https://hvacrschool.com/total-external-static-pressure-tesp-a-basic-review/

## Compare pointwise
Observations from point wise comparison of instruments (pitot and hotwire):
(1) Sign of difference consistent across 20/21 of 25 points.
(2) Most points where sign is different are at edge -- venturi effect of pitot along edge? Or possibly straighter flow on edge.
(3) Degree of difference does not correllate consistently with size of pitot flow. This does not support turbulence hypothesis for difference,
but neither does it disprove it.
West supply duct -- average of three pitot traverses | [8 empty] | East supply duct average of two pitot traverses
| 1 | 2 | 3 | 4 | 5 |  |  |  |  | 1 | 2 | 3 | 4 | 5
5 | 423.3333 | 481 | 601 | 765 | 783.6667 |  |  |  | 5 | 398.3333 | 445.3333 | 450 | 447.3333 | 427.6667
4 | 568.3333 | 606.3333 | 732 | 791 | 890.3333 |  |  |  | 4 | 427 | 439 | 414.3333 | 441 | 459
3 | 515.6667 | 532.6667 | 592.3333 | 745 | 837.6667 |  |  |  | 3 | 453.3333 | 422.6667 | 413 | 419 | 461.3333
2 | 388.3333 | 390.3333 | 480.3333 | 715.6667 | 795.3333 |  |  |  | 2 | 450 | 437.6667 | 430.3333 | 436 | 438
1 | 314 | 315 | 443 | 622 | 740.3333 | Avg | Max | Max/Avg | 1 | 317 | 373.3333 | 377.3333 | 384.3333 | 416.6667 | Avg | Max | Max/Avg
[6 empty] | 602.7867 | 890.3333 | 147.7% | [6 empty] | 423.16 | 461.3333 | 109%
West supply duct hot wire traverse | [8 empty] | East supply duct hot wire traverse
| 544 | 636 | 774 | 893 | 884 |  |  |  |  | 426 | 356 | 416 | 367 | 465
| 585 | 651 | 804 | 900 | 881 |  |  |  |  | 482 | 458 | 426 | 391 | 495
| 595 | 615 | 700 | 803 | 858 |  |  |  |  | 481 | 468 | 447 | 486 | 506
| 457 | 535 | 598 | 761 | 725 |  |  |  |  | 481 | 497 | 513 | 511 | 520
| 303 | 343 | 460 | 631 | 638 | Avg | Max | Max/Avg |  | 345 | 461 | 465 | 490 | 387 | Avg | Max | Max/Avg
[6 empty] | 662.96 | 900 | 135.8% | [6 empty] | 453.6 | 520 | 114.6%
% hotwire above pitot | [8 empty] | % hotwire above pitot | [8 empty] | ABSOLUTE DIFFERENCES
| 28.5% | 32.22% | 28.79% | 16.73% | 12.8% |  |  |  |  | 6.946% | -20.06% | -7.556% | -17.96% | 8.73% |  |  |  | 6.946% | 20.06% | 7.556% | 17.96% | 8.73%
| 2.933% | 7.367% | 9.836% | 13.78% | -1.048% |  |  |  |  | 12.88% | 4.328% | 2.816% | -11.34% | 7.843% |  |  |  | 12.88% | 4.328% | 2.816% | 11.34% | 7.843%
| 15.38% | 15.46% | 18.18% | 7.785% | 2.427% |  |  |  |  | 6.103% | 10.73% | 8.232% | 15.99% | 9.682% |  |  |  | 6.103% | 10.73% | 8.232% | 15.99% | 9.682%
| 17.68% | 37.06% | 24.5% | 6.334% | -8.843% |  |  |  |  | 6.889% | 13.56% | 19.21% | 17.2% | 18.72% |  |  |  | 6.889% | 13.56% | 19.21% | 17.2% | 18.72%
| -3.503% | 8.889% | 3.837% | 1.447% | -13.82% | Avg | Max | Max/Avg |  | 8.833% | 23.48% | 23.23% | 27.49% | -7.12% | Avg | Max | Max/Avg | 8.833% | 23.48% | 23.23% | 27.49% | 7.12%
[6 empty] | 11.39% | 37.06% | 325.4% | [6 empty] | 7.555% | 27.49% | 363.9% | [5 empty] | 12.68%
Average of both instruments | [8 empty] | Average of both instruments
| 483.6667 | 558.5 | 687.5 | 829 | 833.8333 |  |  |  |  | 412.1667 | 400.6667 | 433 | 407.1667 | 446.3333
| 576.6667 | 628.6667 | 768 | 845.5 | 885.6667 |  |  |  |  | 454.5 | 448.5 | 420.1667 | 416 | 477
| 555.3333 | 573.8333 | 646.1667 | 774 | 847.8333 |  |  |  |  | 467.1667 | 445.3333 | 430 | 452.5 | 483.6667
| 422.6667 | 462.6667 | 539.1667 | 738.3333 | 760.1667 |  |  |  |  | 465.5 | 467.3333 | 471.6667 | 473.5 | 479
| 308.5 | 329 | 451.5 | 626.5 | 689.1667 |  |  |  |  | 331 | 417.1667 | 421.1667 | 437.1667 | 401.8333
Correlation of % difference with average | [8 empty] | Correlation of % difference with average
| -0.22948 | [8 empty] | 0.37517

## Daikin Manual
https://www.daikinac.com/content/assets/DOC/EngineeringManuals/2017/Engineering%20Manual-SkyAir-web.pdf
Motor appears to be set to generate .4"H20 -- this is consistent with observed flow, but does not absolutely prove flow
It all roughly fits -- pressure and wattage and observed CFM -- with the standard setting
What if was not initially calibrated and was set at too high voltage? (
Suppose true pressure for 635 CFM was .2" and our flow measurements are just completely off
Running at .4" in a .2" system would generate flows 1.414x as high as rated or approximately 900CFM
Fan power for a set of systems with same flow at each different pressure will be proportional to pressure
So fan power setting in the 2" for 635CFM system is roughly 50 watts subject to fan and motor efficiency curves (since max power may be 200 watts
Running that system at 4" pressure would increase both flow and pressure, leading to a fan load of 50 x 2 x 1.414 -- 141 watts
All of this counterfactual reasoning is speculative as to motor power consumption at different levels. The edge errors are not plausible, but more modest installation errors (.3" or .5") cannot be ruled out, but we have no reason to believe any error.

## Fan and motor efficiency
Electric power to flow relationships are heavily subject to efficiency as well as duct pressure
Bottom line is that since fan and motor efficiency are unknown and can be << 1, can't make any inferences from power to cfm.
Air handleroperating at watts | 94 | [5 empty] | 3.1623 | 5.4772 | 4.3198
Watts are power unit, 1 joule per second
Joule = 1 newton meter
Power in newton-meter/second | 94
divided by pressure in newtons per meter^2 | 100.1337 | 0.402 | inches of water column |  |  | 249.0889 | pascals (n/m2) per inch of water
equals meter^3/sec | 0.93874
cfm | 1987.5598
Motor efficiency and phase AND FAN EFFICIENCY (for example) | 30% | [8 empty] | 286
ESTIMATED CFM | 596.2679
https://www.amca.org/assets/resources/public/pdf/Education%20Modules/AMCA%20210-16.pdf
The problem with the discussion above is that pressure measurements may not really correlate with true fan metrics
Total pressure is a point number versus atmosphere (static plus velocity)
Total fan pressure is the difference of these across the fan inlet to outlet. But the measurement plane is not that in our measurements
Probably have correct static at inlet, not sure about outlet.
My measurements are accurate as to the External Static Pressure of the air handler, but not necessarily the fan per se.
So, they are valid as to the settings of air handler and its relationship to CFM, but not necessarily accurate as to the fan static efficiency.
Would have an even harder time knowing the fan total efficiency since all velocity measurements would be highly turbulent
BUT, the example numbers below as to fan static and total efficiency (when combined with motor efficiency numbers) give plausibility to the low efficiency numbers in the math above
| CFM | Pressure | Factor | BHP | Static Efficiency=(CFM×p)/(6343×BHP) | Reported total efficiency
9x 4 fan from catalog https://oslo.daikinapplied.com/api/sharepoint/getdocument/Doc100/560-1.pdf/ | 900 | 0.5 | 6343 | 0.5 | 0.14189
Our case -- high because not using BHP, using motor pressure | 600 | 0.4 | 6343 | 0.12617 | 0.29988
Big fan in https://content.greenheck.com/public/DAMProd/Original/10002/CS104-13_FEG.pdf | 40000 | 0.13 | 6343 | 6.91 | 0.11864 | 66%
This is a fan manufacturer | 40000 | 0.13 | 6343 | 5.81 | 0.1411 | 54%
Smaller radius fans -- peak total efficiency | [5 empty] | <40%
Study of Sirocco fans -- total efficiency, figure 3 peak total efficiency values | [5 empty] | 50% to 60%
https://downloads.hindawi.com/journals/ijrm/2001/512930.pdf?_gl=1*el7b5t*_ga*OTA0NjUyMDE2LjE3MDczMTA3MDE.*_ga_NF5QFMJT5V*MTcwNzMxMDcwMS4xLjAuMTcwNzMxMDcwNy41NC4wLjA.&_ga=2.79552788.1066158091.1707310701-904652016.1707310701
FEG Explanation
https://www.amca.org/assets/resources/public/userfiles/file/Nospreads_FanEfficGrades.pdf | [5 empty] | 40 to 83%
The guiding document is Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating
https://www.amca.org/assets/resources/public/pdf/Education%20Modules/AMCA%20210-16.pdf
Mandatory explanation:
https://matxansari.files.wordpress.com/2013/11/20140715-curious-definition-fsp-1.pdf
https://matxansari.files.wordpress.com/2013/11/20131102-curious-definition-fsp-2.pdf
https://matxansari.files.wordpress.com/2013/11/20131102-curious-definition-fsp-3.pdf
See also:
https://www.amca.org/assets/resources/public/userfiles/file/cermak_AMCA_web.pdf
Further Small motors may have efficiencies well below 80%, especially at low load
https://www.engineeringtoolbox.com/electrical-motor-efficiency-d_655.html | 78.8% for 1ph
https://www.tytorobotics.com/blogs/articles/what-is-the-average-efficiency-of-an-electric-motor | 85% for 5 to 10kg motors (max)
Efficiencies decline with load
https://www.energy.gov/eere/amo/articles/determining-electric-motor-load-and-efficiency |  |  |  |  | FAN STATIC EFFICIENCY IS BASED ON FAN TOTAL EFFICIENCY AND RATIO OF FSP TO FTP
-- EFFICIENCY IS ALWAYS SYSTEM DEPENDENT; RATINGS ARE FOR COMPARISON
-- FAN STATIC PRESSURE DOES NOT MULTIPLY THROUGH TO A POWER CONCEPT
-- ONLY TOTAL PRESSURE MULTIPLIES THROUGH TO TOTAL OUTPUT POWER
-- EXTERNAL STATIC PRESSURE OF AN AIR HANDLER COULD PROXY FOR FAN STATIC PRESSURE IN DUCT SIZING
-- -- -- BUT IT DOES NOT TRANSLATE INTO TOTAL POWER FROM THE MOTOR BECAUSE OF COIL POWER LOSS
-- -- -- -- EVEN IF INPUT VELOCITY = OUTPUT VELOCITY
The 94 watts power number we have is electric input. We have several efficiency variables after that:
electric to motor shaft power – small motor running at < 1/3 of max wattage, easily 60% efficiency
motor shaft to fan – probably not much loss
fan to air – easily 50% additional losses for small fans, probably especially at low load
Wow. The big lesson for the day. Thank you again.
I am believing that the following relationship should hold in international units (approximating with incompressible flow) :
W = Q * P / E or, alternatively, W / P ​ * E = Q
Where:
W = Watts on the input electric power meter – newton-meter/sec
Q = cubic meters/sec flow
P = fan total pressure in pascals, newton-meter per meter-squared area
E = dimensionless factor (<1) adjusting for inefficiency of fan, drive, motor, etc. combined.
Fan total pressure is measured as the difference between static pressure upstream and downstream from the fan.
My pressure measurement is an external static pressure measurement for the whole unit – downstream from the filter on the return side and downstream from the coil on the supply side, so pressure loss across the coil is an adjustment to make for a fan only.
I get the following measurements of static pressure:
.39 inWG External Static Pressure as defined above,
.17 inWG vs. atmosphere on the supply side plenum
.22 inWG vs. atmosphere on the return side inside the filter just before the fan
I'm guessing that for a fan alone without a coil, the negative pressure before equals the positive pressure after. So, I'm guessing that the coil costs 0.05 inWG in pressure drop and the true fan total pressure difference is .17 +.05+ .22 = .44inWG.
I have measurements of power consistently around 94 watts.
Using the following values in the above equation
W = 94 watts
P = .4 inches WG or 100 pascal (rounding)
E = 60% – just an assumption.
So, flow in cubic meters/sec should be .94 * E which translates into 1987 CFM *60% or 1192 CFM. [1 cubic meter / second = 2 118.88 cubic feet per minute]
The rated flow on high-high (which is our setting) for the Daikin FBQ18PVJU is only 635 CFM and my duct traverses in relatively good spots come up with 593CFM with the hotwire and 545CFM with the Pitot Tube. My balometer measurements are above and below those levels, but both manuals warn to calibrate with a traverse, so I think of the balometers as great for relative flow, but with our funky little low-flow diffusers they do not give convincing absolute flow. The proportions accounted for by each duct do remain consistent across almost all measurements.
I've pasted a page from the Daikin manual below. Our model is FBQ18PVJU.
The Daikin fan is adjustable to produce External Static Pressures ranging across fourteen stops from 50 pascal to 200 pascal. At installation, there is a process to cause it to configure itself to the right level. Even if that was not done, the default rated level is 635 cfm at 100 pascals, which is right about where we are. The 94 watts makes sense because the fan can support ukp to 200 pascals at that flow which would be a duct system requiring roughly double the power or 200 watts, which is getting up towards the stated 286 watt motor capacity at full load ampacity of 1.3 (rated 350 watts). So, I don't think we are misstating the electric power much either up or down.
I also don't see how we could be mismeasuring the pressure in a way that would lead to a much higher value for pressure (which is what we need to bring down the CFM estimate in the equation). I can imagine taking smaller partial pressure values but none of them make sense and would only exacerbate the inconsistency.
So, I'm pretty sure we are in the 600 cfm ballpark. But I don't get what's wrong with the math above which gives a very different result.